## 220KV
Statement of 220-KV MEPCO Consumers For 2020-21
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interr-uptions | Consumers Annual Long Un-planned Interr- uptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interr- uptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interr-uptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | Kot Addu | PARCO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 26 | 0 | 4 | 0 | 36 | 0 | 4 | 0 | 0 | 0 | 0 | 0

## 132KV
Statement of 132-KV MEPCO Consumers For 2020-21
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Circle | Name of Consumer | Consumers Annual Total Short Interr-uptions | Consumers Annual Total Unplanned Long Interr-uptions | Consumers Annual Long Un-planned Interr- uptions Duration (Hrs) | Consumers Annual Total No. of Planned Interr- uptions | Consumers Annual Planned Interr- uptions Duration (Hrs) | Un-Planned Interr- uptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interr- uptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interr- uptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interr-uptions Annual | Annual Agrt: sume of all consumers interr- uptions Duration (Mint:) | SAIFI | SAIDI
1 | Kot Addu | Ahmad Hassan Textile Mills | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 26 | 0 | 4 | 0 | 36 | 0 | 4 | 0 | 0 | 0 | 0 | 0
2 | Cantt Multan | Coca Cola | 3 | 26 | 27 | 5 | 67 | 28 | 0 | 6 | 1 | 26 | 1 | 4 | 1 | 36 | 1 | 4 | 0 | 34 | 5649 | 34 | 5649
3 | Mumtazabad | S.M Foods | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 26 | 0 | 4 | 0 | 36 | 0 | 4 | 0 | 0 | 0 | 0 | 0
4 | City Multan | Colony Textile Mills | 4 | 38 | 28 | 1 | 3 | 42 | 0 | 6 | 1 | 26 | 1 | 4 | 0 | 36 | 0 | 4 | 0 | 43 | 1872 | 43 | 1872
5 | Kot Addu | Ahmad Hassan Textile Mills | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 6 | 0 | 26 | 0 | 4 | 0 | 36 | 0 | 4 | 0 | 0 | 600 | 0 | 600
6 | DG Khan | Al-Hamd Textile Mills | 2 | 1 | 1 | 2 | 10 | 3 | 0 | 6 | 0 | 26 | 0 | 4 | 0 | 36 | 0 | 4 | 0 | 5 | 666 | 5 | 666
7 | Rajanpur | PARCO | 3 | 2 | 1 | 3 | 15 | 5 | 0 | 6 | 0 | 26 | 0 | 4 | 0 | 36 | 0 | 4 | 0 | 8 | 969 | 8 | 969
8 | Kot Chutta | MDC | 5 | 0 | 0 | 1 | 5 | 5 | 0 | 6 | 0 | 26 | 0 | 4 | 0 | 36 | 0 | 4 | 1 | 6 | 315 | 6 | 315
9 | DG Khan | PAEC | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 6 | 0 | 26 | 0 | 4 | 0 | 36 | 0 | 4 | 0 | 1 | 3 | 1 | 3
10 | DG Khan | DG Cement | 3 | 6 | 102 | 7 | 37 | 9 | 6 | 6 | 1 | 26 | 1 | 4 | 1 | 36 | 1 | 4 | 0 | 16 | 8349 | 16 | 8349
|  | Total | 21 | 73 | 159 | 19 | 147 | 93 | 6 | 6 | 3 | 26 | 3 | 4 | 2 | 36 | 2 | 4 | 1 | 113 | 18423 | 113 | 1842.3

## 11-KV Multan
Statement of 11-KV MEPCO Consumers For 2020-21
Multan Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | Cantt | NEW AIR PORT | 41 | 23 | 35.55 | 21 | 87 | 64 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 85 | 7476 | 85 | 7476
2 | Cantt | FORT COLONY | 113 | 7 | 16.3 | 10 | 43.3 | 120 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 130 | 3915 | 130 | 3915
3 | Cantt | PAF | 28 | 4 | 8.3 | 2 | 7 | 32 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 34 | 1002 | 34 | 1002
4 | Cantt | NISHTAR HOSPITAL | 83 | 7 | 27 | 11 | 40 | 90 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 101 | 4269 | 101 | 4269
5 | Cantt | NISHTAR HOSPITAL-II | 47 | 2 | 4.55 | 5 | 24.3 | 49 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 54 | 1872 | 54 | 1872
6 | Cantt | CANTT | 108 | 1 | 0.55 | 17 | 65.25 | 109 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 126 | 4272 | 126 | 4272
7 | Cantt | CHILDREN COMPLEX | 41 | 2 | 3.2 | 5 | 30.2 | 43 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 48 | 2127 | 48 | 2127
8 | Cantt | BURN UNIT | 30 | 5 | 18.5 | 5 | 15.3 | 35 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 40 | 2118 | 40 | 2118
9 | Cantt | PEPSI COLA | 75 | 9 | 19.1 | 15 | 62.1 | 84 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 99 | 5097 | 99 | 5097
10 | Cantt | STATE BANK | 59 | 9 | 17.4 | 11 | 47.4 | 68 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 79 | 4065 | 79 | 4065
11 | Cantt | BOOMANJEE SQUARE | 36 | 8 | 14.4 | 6 | 28.3 | 44 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 50 | 2670 | 50 | 2670
12 | Cantt | MULTAN INSTITUTE OF CARDIOLOGY | 47 | 2 | 5.3 | 4 | 18.3 | 49 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 53 | 1557 | 53 | 1557
13 | Cantt | PEPSICO | 45 | 4 | 8 | 19 | 71 | 49 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 68 | 4875 | 68 | 4875
14 | Cantt | GHOUS FIBER | 35 | 3 | 7 | 25 | 83 | 38 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 63 | 5505 | 63 | 5505
15 | Cantt | IHSAN ELAHI TEX: | 45 | 2 | 16 | 28 | 80 | 47 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 75 | 5895 | 75 | 5895
16 | Cantt | MEHMOODA MAQBOOL MILLS | 43 | 4 | 15 | 20 | 67 | 47 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 67 | 5049 | 67 | 5049
17 | Cantt | ANC FOODS | 41 | 3 | 12 | 24 | 86 | 44 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 68 | 6003 | 68 | 6003
18 | Cantt | THREE STAR HOSIERY UNIT-1 | 44 | 6 | 45 | 24 | 82 | 50 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 74 | 7752 | 74 | 7752
19 | Cantt | GARRISON PUBLIC LIBRARY | 12 | 12 | 22 | 9 | 36 | 24 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 33 | 3516 | 33 | 3516
20 | Cantt | THREE STAR HOSIERY UNIT-2 | 44 | 14 | 39 | 11 | 56 | 58 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 69 | 5832 | 69 | 5832
21 | Cantt | SHABIR FEEDS | 24 | 12 | 30 | 11 | 33.4 | 36 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 47 | 3876 | 47 | 3876
22 | Cantt | ASIA FEEDS | 90 | 10 | 22 | 19 | 71 | 100 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 119 | 5850 | 119 | 5850
23 | Cantt | MEHMOOD TEXTILE MILLS | 43 | 9 | 60 | 24 | 80 | 52 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 76 | 8529 | 76 | 8529
24 | Cantt | KHAWAJA FEEDS | 54 | 8 | 20 | 16 | 60 | 62 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 78 | 4962 | 78 | 4962
25 | Mumtazabad | ANEES TEXTILE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
26 | Mumtazabad | GROUP OF INDUSTRIES | 74 | 16 | 21 | 3 | 9 | 90 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 93 | 2022 | 93 | 2022
27 | Mumtazabad | NISHAT MILL | 32 | 24 | 52.26 | 6 | 26.4 | 56 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 62 | 4815.6 | 62 | 4815.6
28 | Mumtazabad | S.M. FOODS | 19 | 18 | 31.5 | 0 | 0 | 37 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 37 | 1947 | 37 | 1947
29 | Mumtazabad | R.P.T | 52 | 35 | 64.35 | 6 | 27 | 87 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 93 | 5637 | 93 | 5637
30 | Mumtazabad | KIDNEY CENTER | 16 | 9 | 16.5 | 8 | 33.35 | 25 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 33 | 3039 | 33 | 3039
31 | Mumtazabad | A&Z SOLVENT PLANT | 25 | 7 | 17 | 3 | 9 | 32 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 35 | 1635 | 35 | 1635
32 | Mumtazabad | ATM | 14 | 11 | 28.15 | 1 | 4.35 | 25 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 26 | 1992 | 26 | 1992
33 | Mumtazabad | S.M.FOODS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
34 | Mumtazabad | KHAWAJA FAREED HOSPITAL | 14 | 6 | 20.15 | 7 | 24.5 | 20 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 27 | 2721 | 27 | 2721
35 | Mumtazabad | SADIQ TEXTILE MILLS | 122 | 27 | 29.43 | 5 | 14.3 | 149 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 154 | 2989.8 | 154 | 2989.8
36 | Mumtazabad | MUMTAZ OIL MILLS | 86 | 12 | 25.3 | 5 | 14.25 | 98 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 103 | 2631 | 103 | 2631
37 | Mumtazabad | HUSAIN TEXTILE MILLS | 29 | 10 | 22.12 | 4 | 12.15 | 39 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 43 | 2143.2 | 43 | 2143.2
38 | Mumtazabad | AHMAD FINE TEXTILE | 1 | 2 | 9.15 | 4 | 12.15 | 3 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 7 | 1281 | 7 | 1281
39 | Mumtazabad | ALLAH WASAYA SPINNING MILL | 6 | 5 | 5.53 | 4 | 12.15 | 11 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 15 | 1078.8 | 15 | 1078.8
40 | City | CENTRAL JAIL ROAD | 8 | 10 | 24.2 | 6 | 27.15 | 18 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 24 | 3105 | 24 | 3105
41 | City | MIAN NAWAZ SHARIF UNIVERSITY | 30 | 9 | 11 | 7 | 17.45 | 39 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 46 | 1797 | 46 | 1797
42 | City | H.T.M | 56 | 10 | 20.25 | 5 | 24.3 | 66 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 71 | 2841 | 71 | 2841
43 | City | KIDNEY CENTER II | 8 | 9 | 17 | 9 | 27 | 17 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 26 | 2664 | 26 | 2664
44 | Shujabad | SUB JAIL | 7 | 3 | 17 | 3 | 7 | 10 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 13 | 1461 | 13 | 1461
45 | Shujabad | SHABBIR CHICKS | 0 | 3 | 13 | 1 | 16 | 3 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 4 | 1740 | 4 | 1740
46 | Shujabad | T.V. PAK | 2 | 3 | 20 | 3 | 8 | 5 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 8 | 1686 | 8 | 1686
47 | Shujabad | GULSHAN IQBAL | 27 | 38 | 99.2 | 6 | 16.35 | 65 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 71 | 7014 | 71 | 7014
48 | B.Z (Musa Pak) | KHAWAJA TANNERIES | 36 | 9 | 22.52 | 3 | 11.1 | 45 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 48 | 2125.2 | 48 | 2125.2
49 | B.Z (Musa Pak) | WOMEN UNIVERSITY | 18 | 22 | 24.25 | 34 | 141.15 | 40 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 74 | 9978 | 74 | 9978
50 | B.Z (Musa Pak) | BAKHTAWAR AMEEN HOSPITAL | 6 | 0 | 9 | 0 | 27.35 | 6 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 6 | 2199 | 6 | 2199
51 | B.Z (Musa Pak) | MUKHTAR-E-SHEIKH HOSPITAL | 13 | 1 | 2 | 0 | 17.15 | 14 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 14 | 1188 | 14 | 1188
52 | B.Z (Musa Pak) | NFC | 26 | 3 | 34.14 | 3 | 11.1 | 29 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 32 | 2792.4 | 32 | 2792.4
53 | B.Z (Musa Pak) | LAL INDUSTRIES | 26 | 5 | 49 | 3 | 1.3 | 31 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 34 | 3096 | 34 | 3096
54 | B.Z (Musa Pak) | RAJA PUR | 7 | 3 | 16 | 0 | 0 | 10 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 10 | 981 | 10 | 981
55 | B.Z (Musa Pak) | COSLAB | 25 | 8 | 12.24 | 27 | 115.29 | 33 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 60 | 7726.8 | 60 | 7726.8
56 | B.Z (Musa Pak) | METRO CASH & CARRY | 6 | 19 | 46.22 | 27 | 117.19 | 25 | 0 | 30 | 0 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 52 | 9822.6 | 52 | 9822.6
57 | B.Z (Musa Pak) | BZU | 93 | 62 | 120.5 | 26 | 80.2 | 155 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 181 | 12321 | 181 | 12321
58 | S.R Alam | MEHMOOD FEEDS | 47 | 21 | 67.44 | 12 | 55.45 | 68 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 0 | 80 | 7514.4 | 80 | 7514.4
59 | S.R Alam | S.M.FOODS MAKERS | 12 | 7 | 29.28 | 5 | 18.15 | 19 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 24 | 2881.8 | 24 | 2881.8
60 | S.R Alam | H.A.FIBER | 20 | 8 | 28.15 | 1 | 4.55 | 28 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 29 | 2022 | 29 | 2022
61 | S.R Alam | AL-HILAL VEGITABLE GHEE MILLS | 39 | 0 | 8.42 | 9 | 28 | 39 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 48 | 2302.2 | 48 | 2302.2
62 | S.R Alam | Flood Light | 11 | 5 | 26.17 | 7 | 29.45 | 16 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 23 | 3370.2 | 23 | 3370.2
63 | S.R Alam | R.T.M-II | 7 | 9 | 110 | 3 | 4.55 | 16 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 19 | 6894 | 19 | 6894
64 | S.R Alam | ROOMI FABRICS UNIT-2 | 8 | 6 | 19 | 3 | 4.55 | 14 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 17 | 1437 | 17 | 1437
65 | S.R Alam | MASOOD FABRICS | 30 | 8 | 24 | 9 | 29.3 | 38 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 47 | 3288 | 47 | 3288
66 | S.R Alam | ROOMI FABRICS | 13 | 9 | 33 | 3 | 4.45 | 22 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 25 | 2286 | 25 | 2286
67 | S.R Alam | RTM UNIT-4 | 10 | 10 | 341 | 3 | 4.55 | 20 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 23 | 20763 | 23 | 20763
68 | S.R Alam | M.D.M | 2 | 6 | 96 | 5 | 4.55 | 8 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 13 | 6039 | 13 | 6039
69 | S.R Alam | RELIANCE T.M | 16 | 9 | 22 | 3 | 44.57 | 25 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 28 | 4042.2 | 28 | 4042.2
70 | S.R Alam | FCM-6 | 27 | 3 | 5 | 4 | 10.2 | 30 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 34 | 993 | 34 | 993
71 | S.R Alam | SPUN YARN | 19 | 4 | 28 | 11 | 29.3 | 23 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 34 | 3495 | 34 | 3495
72 | S.R Alam | AHMAD FINE UNIT NO.2 | 18 | 16 | 77.15 | 6 | 27.3 | 34 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 40 | 6321 | 40 | 6321
73 | S.R Alam | ASIA FEEDS | 44 | 6 | 6.51 | 2 | 8.3 | 50 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 52 | 1020.6 | 52 | 1020.6
74 | S.R Alam | HUSSAIN TEXTILE MILLS | 24 | 8 | 28 | 5 | 14.55 | 32 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 37 | 2625 | 37 | 2625
75 | S.R Alam | FAZAL CLOTH MILL | 21 | 6 | 19 | 10 | 61.8 | 27 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 37 | 4911 | 37 | 4911
76 | S.R Alam | SHUJA ABAD WEAVING MILL | 9 | 6 | 43 | 7 | 13 | 15 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 22 | 3387 | 22 | 3387
77 | S.R Alam | FCM-8 | 27 | 8 | 81 | 7 | 18 | 35 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 42 | 6021 | 42 | 6021
78 | S.R Alam | FAZAL REHMAN MILLS | 26 | 8 | 50.5 | 9 | 32.3 | 34 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 0 | 43 | 5046 | 43 | 5046
79 | S.R Alam | F.C.M-3 | 34 | 18 | 87.5 | 3 | 4.55 | 52 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 55 | 5625 | 55 | 5625
80 | Cantt | Pearl Residence | 8 | 9 | 37 | 9 | 37.55 | 17 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 26 | 4497 | 26 | 4497
|  |  | 2584 | 755 | 2633.23 | 697 | 2626.5 | 3339 | 0 | 30 | 48 | 44 | 16 | 8 | 30 | 64 | 14 | 140 | 0 | 4036 | 323335.8 | 50.45 | 4041.6975

## 11-KV D.G Khan
Statement of 11-KV MEPCO Consumers For 2020-21
D.G Khan Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | DG Khan | GTM | 29 | 25 | 25 | 12 | 42 | 48 | 6 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 66 | 4107 | 66 | 4107
2 | Kot Chutta | ATM-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
3 | Kot Chutta | AML | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
4 | Kot Chutta | YTM | 18 | 3 | 13 | 4 | 17 | 21 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 25 | 1854 | 25 | 1854
5 | Kot Chutta | SSM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
6 | Kot Chutta | THQ Jampur | 17 | 3 | 3 | 4 | 5 | 20 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 24 | 531 | 24 | 531
7 | Kot Chutta | Arain Fiber | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
8 | DG Khan | RTM | 0 | 0 | 0 | 3 | 6 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 3 | 360 | 3 | 360
9 | Taunsa | THQ Hospital | 40 | 0 | 0 | 6 | 18 | 40 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 46 | 1200 | 46 | 1200
10 | DG Khan | Danish School DG Khan | 52 | 14 | 64 | 16 | 45 | 66 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 0 | 82 | 6696 | 82 | 6696
11 | DG Khan | EXPRESS | 59 | 17 | 54 | 17 | 72 | 75 | 1 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 93 | 7737 | 93 | 7737
12 | DG Khan | Ghazi Medical College | 19 | 0 | 0 | 3 | 4 | 19 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 22 | 297 | 22 | 297
13 | DG Khan | Central Jail | 16 | 1 | 0 | 3 | 7 | 17 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 20 | 468 | 20 | 468
14 | DG Khan | Nagar Nai (PAEC) | 98 | 25 | 15 | 22 | 31 | 123 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 145 | 3054 | 145 | 3054
15 | DG Khan | Water Supply | 97 | 42 | 154 | 21 | 68 | 138 | 1 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 160 | 13611 | 160 | 13611
16 | DG Khan | NDVH Commercial | 19 | 5 | 7 | 8 | 22 | 24 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 32 | 1797 | 32 | 1797
17 | Rajanpur | PAF | 99 | 5 | 7 | 0 | 0 | 104 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 104 | 717 | 104 | 717
18 | Taunsa | Attomic-I | 68 | 5 | 41 | 57 | 144 | 73 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 130 | 11304 | 130 | 11304
19 | Taunsa | PMS | 118 | 22 | 125 | 15 | 35 | 138 | 2 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 0 | 155 | 9954 | 155 | 9954
20 | Taunsa | Atomic-II | 70 | 3 | 11 | 19 | 45 | 73 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 92 | 3570 | 92 | 3570
21 | Rajanpur | Indus Sugar | 55 | 14 | 76 | 0 | 0 | 69 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 69 | 4725 | 69 | 4725
22 | Rajanpur | Danish School Fazilpur | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 24 | 72 | 24 | 72
23 | Rajanpur | District Jail | 32 | 1 | 3 | 0 | 0 | 33 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 33 | 276 | 33 | 276
24 | DG Khan | THQ Level Hospital | 17 | 0 | 0 | 1 | 7 | 17 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 18 | 471 | 18 | 471
25 | DG Khan | MS Teaching Hospital | 20 | 1 | 7 | 2 | 0.25 | 21 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 23 | 495 | 23 | 495
26 | DG Khan | PGSHS | 53 | 9 | 34 | 22 | 76 | 62 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 84 | 6759 | 84 | 6759
27 | Rajanpur | DHQ Hospital | 35 | 1 | 3 | 0 | 0 | 36 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 36 | 285 | 36 | 285
28 | Rajanpur | THQ Hospital (Rojhan) | 10 | 4 | 3 | 0 | 0 | 12 | 2 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 14 | 210 | 14 | 210
|  |  | 947 | 185 | 598 | 211 | 0 | 1253 | 12 | 30 | 12 | 44 | 5 | 8 | 8 | 64 | 3 | 140 | 0 | 1343 | 38721 | 55.9583 | 1613.375

## 11-KV Vehari
Statement of 11-KV MEPCO Consumers For 2020-21
Vehari Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | Vehari | DHQ Hospital | 8 | 2 | 0.17361 | 3 | 0.63194 | 10 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 13 | 72.3333 | 13 | 72.3333
2 | Vehari | S.S. Oil Mills | 7 | 5 | 0.81944 | 2 | 0.22569 | 12 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 14 | 83.7083 | 14 | 83.7083
3 | Vehari | S.S.Feeds | 13 | 1 | 0.60417 | 2 | 0.059028 | 14 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 16 | 78.7917 | 16 | 78.7917
4 | Vehari | T.R.W. Vehari | 0 | 2 | 0.19097 | 3 | 0.41319 | 2 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 5 | 36.25 | 5 | 36.25
5 | Vehari | District Jail Vehari | 7 | 3 | 0.26042 | 4 | 1 | 10 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 14 | 96.625 | 14 | 96.625
6 | Vehari | Industrial Estate | 32 | 5 | 0.71875 | 3 | 0.28819 | 37 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 40 | 156.4167 | 40 | 156.4167
7 | Burewala | BTM-3 | 5 | 5 | 35 | 5 | 9 | 9 | 1 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 15 | 2655 | 15 | 2655
8 | Burewala | Royal Garden | 16 | 1 | 11 | 6 | 17 | 17 | 1 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 1 | 23 | 1728 | 23 | 1728
|  |  | 72 | 23 | 48.7674 | 17 | 28.6181 | 111 | 2 | 30 | 1 | 44 | 0 | 8 | 2 | 64 | 0 | 140 | 1 | 112 | 4859.125 | 14 | 607.3906

## 11-KV Bahawalpur
Statement of 11-KV MEPCO Consumers For 2020-21
Bahawalpur Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | City Bahawalpur | Allied Solvent | 4 | 0 | 1.0347 | 4 | 0.55208 | 4 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 8 | 107.2083 | 8 | 107.2083
2 | City Bahawalpur | Civil Hospital | 20 | 2 | 1.1111 | 4 | 0.55208 | 22 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 26 | 159.7917 | 26 | 159.7917
3 | City Bahawalpur | Solar Park | 41 | 9 | 2.375 | 5 | 0.95833 | 50 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 55 | 323 | 55 | 323
4 | Lodhran | Pakiza Flour Mills | 1 | 1 | 0.32 | 2 | 6.15 | 2 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 4 | 391.2 | 4 | 391.2
5 | Lodhran | Aziz Feeds | 61 | 16 | 44.35 | 7 | 24.3 | 77 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 84 | 4302 | 84 | 4302
6 | Lodhran | D.h.q | 35 | 18 | 43.23 | 10 | 22.1 | 53 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 63 | 4024.8 | 63 | 4024.8
7 | Lodhran | District Jail Lodhran | 63 | 13 | 43.2 | 7 | 25.15 | 76 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 83 | 4290 | 83 | 4290
8 | Lodhran | Khawaja Bashir | 18 | 4 | 18.5 | 5 | 19 | 22 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 27 | 2304 | 27 | 2304
9 | Lodhran | Nasir Salvent | 24 | 10 | 28.08 | 9 | 32.05 | 34 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 43 | 3679.8 | 43 | 3679.8
10 | AP East | MES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
11 | Model Town | Ashraf Sugar | 15 | 4 | 0 | 3 | 8 | 19 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 22 | 525 | 22 | 525
12 | Model Town | Op. Theater | 63 | 28 | 39.15 | 1 | 4.05 | 91 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 92 | 2781 | 92 | 2781
13 | Model Town | Asia Ghee | 26 | 8 | 0 | 6 | 25 | 34 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 40 | 1578 | 40 | 1578
14 | Model Town | Bahawalpur Steel Mill | 19 | 4 | 0 | 14 | 46 | 23 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 37 | 2817 | 37 | 2817
15 | Model Town | Pol Army(p.t.m) | 17 | 4 | 0 | 9 | 35 | 21 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 30 | 2151 | 30 | 2151
16 | Model Town | Power Steel Mills | 3 | 2 | 0 | 16 | 31 | 5 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 21 | 1869 | 21 | 1869
17 | Model Town | Shamim Oil Mill | 10 | 8 | 0 | 8 | 34 | 18 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 26 | 2070 | 26 | 2070
18 | Model Town | Sinco Steel Mills | 3 | 0 | 0 | 13 | 46 | 3 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 16 | 2769 | 16 | 2769
19 | Model Town | Air Port | 11 | 0 | 55 | 0 | 0 | 11 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 11 | 3333 | 11 | 3333
20 | Model Town | BVH | 30 | 3 | 1.5153 | 22 | 5.1285 | 33 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 55 | 488.625 | 55 | 488.625
21 | Model Town | Kidney Center | 43 | 12 | 72.2 | 2 | 9.25 | 55 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 57 | 5016 | 57 | 5016
22 | Model Town | Mes New Cantt | 58 | 10 | 0.72222 | 0 | 0 | 68 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 68 | 217.3333 | 68 | 217.3333
23 | Model Town | Mes.2 | 40 | 4 | 23.1 | 1 | 4.05 | 44 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 45 | 1749 | 45 | 1749
24 | Model Town | Mes-i | 181 | 23 | 59.43 | 13 | 14.05 | 204 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 1 | 217 | 4951.8 | 217 | 4951.8
25 | Model Town | Punjab College | 21 | 4 | 30.2 | 30.2 | 17.55 | 25 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 55.2 | 2928 | 55.2 | 2928
26 | Model Town | Uni. Animal Sciences | 69 | 10 | 0.76389 | 145 | 144.3 | 79 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 224 | 8910.8333 | 224 | 8910.8333
27 | Model Town | University | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
28 | Model Town | New Central Jail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
29 | Model Town | Radio Pakistan | 22 | 17 | 87.1 | 4 | 17.28 | 39 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 43 | 6328.8 | 43 | 6328.8
30 | Model Town | Alain_paper | 11 | 7 | 39.05 | 1 | 4.05 | 18 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 19 | 2619 | 19 | 2619
31 | Hasil Pur | Water Works | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
|  |  | 909 | 221 | 590.4322 | 341.2 | 575.521 | 1130 | 0 | 30 | 14 | 44 | 5 | 8 | 10 | 64 | 1 | 140 | 1 | 1471.2 | 72684.1917 | 43.2706 | 2137.7703

## 11-KV Sahiwal
Statement of 11-KV MEPCO Consumers For 2020-21
Sahiwal Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | Sahiwal-I | D.H.Q Teaching Hospital | 23 | 7 | 10:35 | 27 | 47:18 | 30 | 0 | 30 | 0 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 57 | 213.7083 | 57 | 213.7083
2 | Sahiwal-I | A.A Natural Polymer | 14 | 8 | 30:26 | 7 | 33:25 | 22 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 29 | 201.625 | 29 | 201.625
3 | Sahiwal-I | Medical College | 13 | 1 | 01:40 | 7 | 20:55 | 14 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 21 | 95.4583 | 21 | 95.4583
4 | Sahiwal-I | Coal Fired Power Plant | 4 | 1 | 01:42 | 5 | 23:45 | 5 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 10 | 75.625 | 10 | 75.625
5 | Sahiwal-I | Nargis Textile | 22 | 2 | 3.05 | 5 | 16:50 | 24 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 1 | 140 | 0 | 29 | 291.0833 | 29 | 291.0833
6 | Sahiwal-I | Asia Poultary Feed | 28 | 1 | 08:17 | 5 | 24:55 | 29 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 34 | 167 | 34 | 167
7 | Sahiwal-II | Kashmir Edible | 38 | 19 | 102:13 | 6 | 36:45 | 56 | 1 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 63 | 461.4167 | 63 | 461.4167
8 | Sahiwal-II | MA FOODS | 16 | 10 | 38:16 | 7 | 48:55 | 26 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 33 | 265.9583 | 33 | 265.9583
9 | Sahiwal-II | Engro Foods | 18 | 16 | 180:17 | 6 | 27:55 | 32 | 2 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 40 | 574.5 | 40 | 574.5
10 | Sahiwal-II | Supreme | 13 | 14 | 88:47 | 4 | 19:05 | 25 | 2 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 31 | 308.6667 | 31 | 308.6667
11 | Sahiwal-II | Leather Coordinator | 5 | 6 | 32:10 | 5 | 29:55 | 11 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 16 | 170.2083 | 16 | 170.2083
12 | Sahiwal-II | Safia Rice Mills | 23 | 19 | 16:02 | 6 | 30:20 | 39 | 3 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 48 | 184.9167 | 48 | 184.9167
13 | Sahiwal-II | Hascol | 42 | 31 | 272:07 | 5 | 22:50 | 71 | 2 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 78 | 863.375 | 78 | 863.375
14 | Sahiwal-II | Lalazar Spinning Mills | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
15 | Sahiwal-II | Central Jail | 19 | 2 | 01:42 | 15 | 50:50 | 21 | 0 | 30 | 0 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 36 | 188.3333 | 36 | 188.3333
16 | Sahiwal-II | High Security Prison | 50 | 0 | 0 | 9 | 07:03 | 50 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 59 | 167.625 | 59 | 167.625
17 | Sahiwal-II | Adam Milk | 6 | 6 | 15:32 | 7 | 39:40 | 12 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 19 | 156 | 19 | 156
18 | Sahiwal-II | Seed Corporation | 23 | 21 | 51:33 | 6 | 27:40 | 43 | 1 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 50 | 267.0417 | 50 | 267.0417
19 | Sahiwal-II | Mian Textile | 4 | 3 | 06:10 | 3 | 08:40 | 7 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 10 | 49.0833 | 10 | 49.0833
20 | Sahiwal-II | Suraj Fertilizer | 10 | 6 | 12:10 | 4 | 10:08 | 16 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 20 | 85.75 | 20 | 85.75
21 | Sahiwal-II | Tareen Cold Storage | 6 | 3 | 04:10 | 2 | 04:30 | 9 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 11 | 39.6667 | 11 | 39.6667
22 | Sahiwal-II | Eden Milk | 4 | 3 | 06:10 | 4 | 08:10 | 7 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 11 | 47.8333 | 11 | 47.8333
23 | Sahiwal-II | Adam Cold Storage | 7 | 4 | 08:10 | 3 | 07:40 | 11 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 14 | 60.5833 | 14 | 60.5833
24 | Sahiwal-II | SB Feeds | 5 | 2 | 06:07 | 2 | 04:10 | 7 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 9 | 40.7083 | 9 | 40.7083
25 | Sahiwal-II | Shoaib Suleman-I | 10 | 4 | 08:10 | 4 | 08:10 | 14 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 18 | 70.8333 | 18 | 70.8333
26 | Sahiwal-II | Shoaib Suleman-II | 8 | 2 | 05:10 | 3 | 06:10 | 10 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 13 | 52.3333 | 13 | 52.3333
27 | Sahiwal-II | H.T.M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
28 | CCW | Chohdary Feed | 10 | 2 | 18:05 | 7 | 34:10 | 11 | 1 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 19 | 160.625 | 19 | 160.625
29 | CCW | Imtiaz Textile | 10 | 2 | 16:30 | 11 | 39:25 | 11 | 1 | 30 | 0 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 23 | 169.7917 | 23 | 169.7917
30 | CCW | THQ Hospital | 14 | 3 | 19:40 | 7 | 29:35 | 16 | 1 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 24 | 165.125 | 24 | 165.125
31 | A/W | THQ Hospital Arifwala | 146 | 35 | 03:20 | 16 | 24:30 | 181 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 1 | 197 | 507.5833 | 197 | 507.5833
32 | A/W | Asia Poultry Feeds | 3 | 1 | 21:55 | 1 | 02:50 | 4 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 5 | 70.875 | 5 | 70.875
33 | PPN | DHQ Pakpattan | 7 | 1 | 04:31 | 1 | 03:45 | 8 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 9 | 41.6667 | 9 | 41.6667
34 | PPN | Ittefaq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
35 | PPN | Fauji Fresh & Freeze | 11 | 2 | 07:55 | 3 | 12:00 | 13 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 16 | 82.7917 | 16 | 82.7917
36 | PPN | Jail | 0 | 2 | 01:10 | 1 | 00:30 | 2 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 3 | 4.1667 | 3 | 4.1667
37 | PPN | Zubair Feed | 0 | 3 | 53:42 | 4 | 24:22 | 1 | 2 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 1 | 140 | 0 | 7 | 195.1667 | 7 | 195.1667
|  | Total | 601 | 235 | 3.05 | 200 | 0 | 838 | 14 | 30 | 7 | 44 | 29 | 8 | 5 | 64 | 31 | 140 | 1 | 1036 | 1986 | 31.3939 | 60.1818

## 11-KV R.Y Khan
Statement of 11-KV MEPCO Consumers For 2020-21
R.Y Khan Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | R.Y.Khan | Lever | 3 | 2 | 0.47 | 5 | 29 | 5 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 10 | 1777.2 | 10 | 1777.2
2 | R.Y.Khan | ATM-I | 9 | 2 | 0.21 | 7 | 29 | 11 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 18 | 1779.6 | 18 | 1779.6
3 | R.Y.Khan | ATM-II | 25 | 4 | 0.47 | 7 | 29 | 29 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 36 | 1843.2 | 36 | 1843.2
4 | R.Y.Khan | AOTM | 40 | 4 | 0.48 | 7 | 29 | 44 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 51 | 1888.8 | 51 | 1888.8
5 | R.Y.Khan | ATM-IV | 8 | 1 | 0.26 | 9 | 38 | 9 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 18 | 2319.6 | 18 | 2319.6
6 | R.Y.Khan | Air Port | 142 | 14 | 5.79 | 11 | 42 | 156 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 1 | 167 | 3293.4 | 167 | 3293.4
7 | R.Y.Khan | Sheikh Zayed Hospital | 52 | 13 | 1.81 | 17 | 66 | 65 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 82 | 4224.6 | 82 | 4224.6
8 | R.Y.Khan | Coca Cola | 12 | 2 | 0.52 | 7 | 29 | 14 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 21 | 1807.2 | 21 | 1807.2
9 | R.Y.Khan | Abu Dahbi | 73 | 10 | 2.75 | 11 | 46 | 83 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 94 | 3144 | 94 | 3144
10 | R.Y.Khan | Anwar & Co. | 8 | 1 | 0.7 | 9 | 37 | 9 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 18 | 2286 | 18 | 2286
11 | R.Y.Khan | AL-Khair | 18 | 1 | 0.27 | 8 | 33 | 19 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 27 | 2050.2 | 27 | 2050.2
12 | R.Y.Khan | Suriyan | 94 | 12 | 2.23 | 5 | 21 | 106 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 111 | 1675.8 | 111 | 1675.8
13 | R.Y.Khan | Medical College | 18 | 4 | 0.93 | 12 | 51 | 22 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 34 | 3169.8 | 34 | 3169.8
14 | R.Y.Khan | District Jail | 15 | 0 | 0 | 2 | 8 | 15 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 17 | 525 | 17 | 525
15 | Khan Pur | Haleeb | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 13 | 39 | 13 | 39
16 | Khan Pur | Mehmood Cotton | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 13 | 39 | 13 | 39
17 | Khan Pur | 500 kV Grid Station | 18 | 1 | 0 | 0 | 0 | 19 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 19 | 54 | 19 | 54
18 | Sadiq Abad | AJFM | 15 | 4 | 0.35 | 1 | 6.5 | 19 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 20 | 456 | 20 | 456
19 | Sadiq Abad | Crown Motors | 26 | 3 | 2.12 | 24 | 103.5 | 29 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 53 | 6415.2 | 53 | 6415.2
20 | Sadiq Abad | R.Y.K Industrial Estate | 64 | 5 | 7 | 16 | 88 | 69 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 85 | 5892 | 85 | 5892
21 | Sadiq Abad | Shan Flour Mills | 29 | 6 | 2.4 | 1 | 6.5 | 35 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 36 | 621 | 36 | 621
22 | Sadiq Abad | China Estate Nawaz Abad | 16 | 5 | 14.45 | 0 | 0 | 21 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 21 | 915 | 21 | 915
23 | Sadiq Abad | China Estate J.D.Wali | 7 | 2 | 8 | 0 | 0 | 9 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 9 | 501 | 9 | 501
24 | Sadiq Abad | Sugar Mills JDW | 7 | 1 | 0.1 | 0 | 0 | 8 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 8 | 27 | 8 | 27
25 | Sadiq Abad | J.K Dairy | 7 | 1 | 2.05 | 0 | 0 | 8 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 8 | 144 | 8 | 144
|  |  | 732 | 98 | 53.36 | 159 | 691.5 | 830 | 0 | 30 | 7 | 44 | 0 | 8 | 8 | 64 | 3 | 140 | 1 | 989 | 46887.6 | 39.56 | 1875.504

## 11-KV Muzaffargarh
Statement of 11-KV MEPCO Consumers For 2020-21
Muzaffargarh Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | Muzaffargarh | Imperial Textile Mills | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
2 | Muzaffargarh | Appolo Textile Mills | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
3 | Muzaffargarh | AZGARD-9 | 14 | 2 | 3 | 1 | 7 | 16 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 17 | 642 | 17 | 642
4 | Muzaffargarh | Mishal Sania (MTM-I) | 12 | 3 | 4 | 4 | 10 | 15 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 19 | 876 | 19 | 876
5 | Muzaffargarh | Hashir Textile-II | 13 | 2 | 2 | 7 | 11 | 15 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 22 | 819 | 22 | 819
6 | Muzaffargarh | Husnain Textil (Hashir-III) | 13 | 0 | 0 | 5 | 23 | 13 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 18 | 1419 | 18 | 1419
7 | Muzaffargarh | Indus Textile Mills | 39 | 10 | 76 | 16 | 69 | 49 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 1 | 140 | 0 | 65 | 8817 | 65 | 8817
8 | Muzaffargarh | Sunrays Textile Mills | 16 | 6 | 7 | 19 | 84 | 22 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 41 | 5508 | 41 | 5508
9 | Muzaffargarh | Fazal Cloth Mills-I | 13 | 4 | 16 | 14 | 49 | 17 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 31 | 3939 | 31 | 3939
10 | Muzaffargarh | Fazal Cloth Mills-II | 8 | 3 | 4 | 3 | 19 | 11 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 14 | 1404 | 14 | 1404
11 | Muzaffargarh | Fazal Cloth Mills-IV | 2 | 2 | 2 | 5 | 27 | 4 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 9 | 1746 | 9 | 1746
12 | Muzaffargarh | FCM (Open End) | 3 | 2 | 2 | 5 | 27 | 5 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 10 | 1749 | 10 | 1749
13 | Muzaffargarh | TATA Textile Mills | 11 | 16 | 116 | 6 | 16 | 25 | 2 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 33 | 7953 | 33 | 7953
14 | Muzaffargarh | TATA Textile Mills #02 | 16 | 6 | 31 | 4 | 13 | 22 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 26 | 2688 | 26 | 2688
15 | Muzaffargarh | CTM (Mehmood Text: Mills) | 40 | 12 | 68 | 7 | 37 | 52 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 59 | 6420 | 59 | 6420
16 | Muzaffargarh | Masood Textile Mills | 5 | 2 | 5 | 3 | 7 | 7 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 10 | 735 | 10 | 735
17 | Muzaffargarh | Fatima Textile Mills | 12 | 7 | 53 | 3 | 3 | 19 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 22 | 3396 | 22 | 3396
18 | Muzaffargarh | Nafees Cloth Mills | 12 | 2 | 5 | 0 | 8 | 14 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 14 | 816 | 14 | 816
19 | Muzaffargarh | Thal Jute Mills | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 3 | 9 | 3 | 9
20 | Muzaffargarh | TIKA Hospital | 13 | 0 | 0 | 2 | 2 | 13 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 15 | 159 | 15 | 159
21 | Muzaffargarh | Mehmood Textile | 26 | 13 | 55 | 16 | 29 | 39 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 0 | 55 | 5118 | 55 | 5118
22 | Muzaffargarh | District Jail M/Garh | 4 | 0 | 0 | 2 | 0 | 4 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 6 | 12 | 6 | 12
23 | Muzaffargarh | DHQ Hospital, M/Garh | 17 | 2 | 1 | 3 | 8 | 19 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 22 | 591 | 22 | 591
24 | Muzaffargarh | Tayeb Eurdgon-I | 7 | 0 | 0 | 1 | 0 | 7 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 8 | 21 | 8 | 21
25 | Muzaffargarh | Tayeb Eurdgon-II | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 2 | 60 | 2 | 60
26 | Muzaffargarh | Fatima Energy Ltd (FEL) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
27 | Kot Addu | Khokhar Textile Mills | 4 | 4 | 25 | 8 | 17 | 8 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 16 | 2532 | 16 | 2532
28 | Kot Addu | Faisal Asad Textile Mills | 6 | 6 | 11 | 5 | 18 | 12 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 17 | 1758 | 17 | 1758
29 | Kot Addu | Maqbool Textile Mills-I | 3 | 1 | 1 | 9 | 31 | 4 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 13 | 1929 | 13 | 1929
30 | Kot Addu | Maqbool Textile Mills-II | 7 | 3 | 3 | 6 | 30 | 10 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 16 | 2001 | 16 | 2001
31 | Kot Addu | Mehmood Textile-6 | 1 | 5 | 2 | 6 | 28 | 6 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 12 | 1803 | 12 | 1803
32 | Kot Addu | Fatima Sugar Mills | 37 | 6 | 51 | 2 | 1 | 43 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 45 | 3231 | 45 | 3231
33 | Kot Addu | PSO | 56 | 7 | 17 | 12 | 18 | 63 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 75 | 2268 | 75 | 2268
34 | Kot Addu | Asia Poultry Feeds | 137 | 2 | 53 | 11 | 56 | 139 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 0 | 150 | 6951 | 150 | 6951
35 | Kot Addu | THQ Hospital | 137 | 2 | 53 | 12 | 26 | 139 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 0 | 151 | 5151 | 151 | 5151
36 | Kot Addu | Fossil Energy | 30 | 4 | 5 | 0 | 5 | 34 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 34 | 690 | 34 | 690
37 | Layyah | Co-Generation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
38 | Layyah | District Jail Layyah | 5 | 0 | 0 | 0 | 40 | 5 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 5 | 2415 | 5 | 2415
39 | Layyah | DHQ Hospital Layyah | 10 | 5 | 6 | 16 | 44 | 15 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 31 | 3030 | 31 | 3030
40 | Layyah | THQ Chobara | 15 | 10 | 0 | 10 | 27 | 25 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 35 | 1665 | 35 | 1665
41 | Layyah | THQ Chowk Azam | 17 | 4 | 13 | 9 | 19 | 21 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 30 | 1971 | 30 | 1971
42 | Alipur | Shakir Ejaz | 22 | 2 | 12 | 15 | 44 | 24 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 39 | 3426 | 39 | 3426
43 | Alipur | Civil Aviation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
44 | Alipur | Saqib Brothers | 16 | 1 | 2 | 17 | 60 | 17 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 34 | 3768 | 34 | 3768
45 | Alipur | THQ Hospital | 35 | 4 | 13 | 31 | 99 | 39 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 1 | 140 | 0 | 70 | 6825 | 70 | 6825
|  |  | 837 | 160 | 717 | 297 | 1013 | 995 | 2 | 30 | 9 | 44 | 8 | 8 | 14 | 64 | 3 | 140 | 0 | 1294 | 106311 | 30.093 | 2472.3488

## 11-KV Bahawal Nagar
Statement of 11-KV MEPCO Consumers For 2020-21
Bahawal Nagar Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | BAHAWAL NAGAR | QADRI TEXT TILE MILLS | 22 | 5 | 0.80486 | 8 | 1.2042 | 27 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 35 | 186.5417 | 35 | 186.5417
2 |  | NEW CITY HOUSING SCHEME | 46 | 8 | 0.76597 | 9 | 1.5278 | 54 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 63 | 275.625 | 63 | 275.625
3 |  | DISTRICT JAIL ROAD | 20 | 8 | 0.68611 | 7 | 1.2451 | 28 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 35 | 175.875 | 35 | 175.875
4 |  | HOSPITAL | 15 | 1 | 0.25694 | 8 | 1.0604 | 16 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 24 | 124.0417 | 24 | 124.0417
5 |  | CANTT | 67 | 1 | 0.32153 | 7 | 1.1979 | 68 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 75 | 292.1667 | 75 | 292.1667
6 |  | M/ABAD I | 81 | 10 | 39.1076 | 9 | 6.0271 | 90 | 1 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 100 | 2951.0833 | 100 | 2951.0833
7 | HAROON ABAD | THQ HAROONABAD | 162 | 15 | 0.54583 | 29 | 2.6042 | 177 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 1 | 206 | 675 | 206 | 675
8 |  | MODEL AVENUE | 176 | 30 | 1.7681 | 39 | 3.8201 | 206 | 0 | 30 | 1 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 1 | 245 | 863.2917 | 245 | 863.2917
9 |  | THQ FORTABBAS | 0 | 2 | 0.094444 | 8 | 1.4993 | 2 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 10 | 95.625 | 10 | 95.625
10 | CHISHTIAN | THQ CHISHTIAN | 1 | 0 | 0 | 1 | 0.041667 | 1 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 2 | 5.5 | 2 | 5.5
11 |  | 03-MARLA SCHEME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 0 | 0 | 0 | 0
|  |  | 590 | 80 | 44.3514 | 125 | 20.2278 | 669 | 1 | 30 | 5 | 44 | 0 | 8 | 4 | 64 | 0 | 140 | 2 | 795 | 5644.75 | 113.5714 | 806.3929

## 11-KV Khanewal
Statement of 11-KV MEPCO Consumers For 2020-21
Khanewal Circle
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Name of Division | Name of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | Khanewal | Jadeed | 86 | 19 | 122.1 | 12 | 44.5 | 105 | 0 | 30 | 1 | 44 | 1 | 8 | 1 | 64 | 0 | 140 | 0 | 117 | 10254 | 117 | 10254
2 | Khanewal | Express (Jail) | 25 | 7 | 42.44 | 2 | 12.15 | 32 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 34 | 3350.4 | 34 | 3350.4
3 | Khanewal | Express (DHQ) | 28 | 6 | 41.05 | 2 | 12.2 | 34 | 0 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 36 | 3279 | 36 | 3279
4 | Khanewal | MES | 81 | 6 | 48.51 | 4 | 22.2 | 87 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 91 | 4485.6 | 91 | 4485.6
5 | Khanewal | Seed Corporation | 18 | 3 | 31.55 | 3 | 16.35 | 21 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 24 | 2928 | 24 | 2928
6 | Khanewal | Unilever | 30 | 8 | 45.25 | 5 | 24.05 | 38 | 0 | 30 | 1 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 43 | 4248 | 43 | 4248
7 | Khanewal | ATM | 7 | 2 | 3 | 8 | 11 | 9 | 0 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 17 | 861 | 17 | 861
8 | Kabirwala | HIRAJ COTTON | 3 | 0 | 4 | 3 | 11 | 2 | 1 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 1 | 140 | 0 | 6 | 909 | 6 | 909
9 | Mian Channu | Monnowal Textile Mills | 15 | 2 | 17.25 | 9 | 29.2 | 16 | 1 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 26 | 2832 | 26 | 2832
10 | Mian Channu | Spintex Mills | 0 | 0 | 0 | 6 | 23.1 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 6 | 1386 | 6 | 1386
11 | Mian Channu | Jamhoor Textile Mills | 25 | 10 | 30.5 | 7 | 19.5 | 34 | 1 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 42 | 3075 | 42 | 3075
12 | Mian Channu | J-K Sugar Mill | 5 | 0 | 0 | 4 | 3 | 5 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 9 | 195 | 9 | 195
13 | Mian Channu | Qureshi Textile Mills | 8 | 3 | 13.25 | 11 | 44 | 10 | 1 | 30 | 0 | 44 | 0 | 8 | 1 | 64 | 0 | 140 | 0 | 22 | 3459 | 22 | 3459
14 | Mian Channu | Awais Usama Paper Mills | 18 | 14 | 15.3 | 8 | 23.45 | 31 | 1 | 30 | 1 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 40 | 2379 | 40 | 2379
15 | Kabirwala | MASOOD SPING | 0 | 0 | 0 | 4 | 21.2 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 4 | 1272 | 4 | 1272
16 | Kabirwala | MASOOD SPING 2 | 1 | 0 | 0 | 1 | 2.2 | 1 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 2 | 135 | 2 | 135
17 | Kabirwala | MASOOD FABRIC | 1 | 0 | 0 | 1 | 2.2 | 1 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 2 | 135 | 2 | 135
18 | Kabirwala | HUSSAIN TEXTILE | 4 | 1 | 37.1 | 2 | 12.35 | 5 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 7 | 2979 | 7 | 2979
19 | Kabirwala | MULTAN FEEDS | 0 | 0 | 0 | 4 | 20.18 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 4 | 1210.8 | 4 | 1210.8
20 | Kabirwala | NESTLE MILK PACK | 7 | 5 | 57.21 | 2 | 5.21 | 12 | 0 | 30 | 0 | 44 | 1 | 8 | 0 | 64 | 0 | 140 | 0 | 14 | 3766.2 | 14 | 3766.2
21 | Kabirwala | KABIR POLY | 1 | 0 | 0 | 3 | 12.15 | 1 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 4 | 732 | 4 | 732
22 | Kabirwala | F.B Feed | 0 | 0 | 5.11 | 1 | 3.2 | 0 | 0 | 30 | 0 | 44 | 0 | 8 | 0 | 64 | 0 | 140 | 0 | 1 | 498.6 | 1 | 498.6
|  |  | 363 | 84 | 513.62 | 94 | 363.39 | 444 | 5 | 30 | 7 | 44 | 4 | 8 | 4 | 64 | 1 | 140 | 0 | 541 | 53709.6 | 22.5417 | 2237.9

## 400-220 (Urban) Multan
Statement of 400/220 V MEPCO Consumers For 2020-21
Multan Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | Cantt | KOTLA WARIS SHAH | Urban | 6080 | 22 | 6.6 | 40128 | 10 | 25.4 | 185318.4 | 25.4 | 185318.4 | 12 | 72960 | 26.4 | 160512 | 32 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 298406.4 | 20870208 | 49.08 | 3432.6
2 | Cantt | ALLAMA IQBAL | Urban | 2889 | 151 | 45.3 | 130871.7 | 16 | 121.7 | 421909.56 | 121.7 | 421909.56 | 14 | 40446 | 46.3 | 133760.7 | 167 | 0 | 60 | 2889 | 88 | 2889 | 16 | 0 | 80 | 0 | 275 | 0 | 593227.26 | 33732830.7 | 205.34 | 11676.3
3 | Cantt | ISMAILABAD | Urban | 3575 | 153 | 45.9 | 164092.5 | 26 | 133.1 | 570999 | 133.1 | 570999 | 14 | 50050 | 46.5 | 166237.5 | 179 | 0 | 60 | 3575 | 88 | 3575 | 16 | 0 | 80 | 0 | 275 | 0 | 785141.5 | 44726467.5 | 219.62 | 12510.9
4 | Cantt | QUAID-I-AZAM ROAD | Urban | 3480 | 120 | 36 | 125280 | 19 | 103 | 430128 | 103 | 430128 | 14 | 48720 | 46.5 | 161820 | 139 | 0 | 60 | 3480 | 88 | 3480 | 16 | 0 | 80 | 0 | 275 | 0 | 604128 | 35892720 | 173.6 | 10314
5 | Cantt | HIGH COURT | Urban | 3877 | 212 | 63.6 | 246577.2 | 19 | 167.4 | 778811.76 | 167.4 | 778811.76 | 14 | 54278 | 51.4 | 199277.8 | 231 | 0 | 60 | 3877 | 88 | 3877 | 16 | 0 | 80 | 0 | 275 | 0 | 1079666.96 | 59425105.2 | 278.48 | 15327.6
6 | Cantt | JINNAH TOWN | Urban | 6417 | 108 | 32.4 | 207910.8 | 11 | 86.6 | 666854.64 | 86.6 | 666854.64 | 20 | 128340 | 85.5 | 548653.5 | 119 | 0 | 60 | 6417 | 88 | 6417 | 16 | 6417 | 80 | 6417 | 275 | 0 | 1003105.44 | 73554220.8 | 156.32 | 11462.4
7 | Cantt | SURAJ MIANI ROAD | Urban | 5020 | 93 | 27.9 | 140058 | 12 | 77.1 | 464450.4 | 77.1 | 464450.4 | 14 | 70280 | 56.2 | 282124 | 105 | 0 | 60 | 5020 | 88 | 5020 | 16 | 0 | 80 | 0 | 275 | 0 | 674788.4 | 45214638 | 134.42 | 9006.9
8 | Cantt | NEW JINNAH TOWN | Urban | 4608 | 100 | 30 | 138240 | 48 | 118 | 652492.8 | 118 | 652492.8 | 7 | 32256 | 25.54 | 117688.32 | 148 | 0 | 60 | 4608 | 88 | 4608 | 16 | 0 | 80 | 0 | 275 | 0 | 822988.8 | 46625587.2 | 178.6 | 10118.4
9 | Cantt | NEW RAZA HALL | Urban | 3645 | 86 | 25.8 | 94041 | 43 | 103.2 | 451396.8 | 103.2 | 451396.8 | 8 | 29160 | 29.2 | 106434 | 129 | 0 | 60 | 3645 | 88 | 3645 | 16 | 0 | 80 | 0 | 275 | 0 | 574597.8 | 33751971 | 157.64 | 9259.8
10 | Cantt | NEW EXPRESS | Urban | 4803 | 108 | 32.4 | 155617.2 | 50 | 125.6 | 723908.16 | 125.6 | 723908.16 | 7 | 33621 | 20.13 | 96684.39 | 158 | 0 | 60 | 4803 | 88 | 4803 | 16 | 0 | 80 | 0 | 275 | 0 | 913146.36 | 49702404.6 | 190.12 | 10348.2
11 | Cantt | ABDALI ROAD | Urban | 3919 | 159 | 47.7 | 186936.3 | 26 | 137.3 | 645694.44 | 137.3 | 645694.44 | 13 | 50947 | 57.1 | 223774.9 | 185 | 0 | 60 | 3919 | 88 | 3919 | 16 | 0 | 80 | 0 | 275 | 0 | 883577.74 | 52728969.3 | 225.46 | 13454.7
12 | Cantt | NAWAN SHEHAR | Urban | 5999 | 155 | 46.5 | 278953.5 | 29 | 137.5 | 989835 | 137.5 | 989835 | 13 | 77987 | 50.4 | 302349.6 | 184 | 0 | 60 | 5999 | 88 | 5999 | 16 | 0 | 80 | 0 | 275 | 0 | 1346775.5 | 78367936.5 | 224.5 | 13063.5
13 | Cantt | EXPRESS | Urban | 4754 | 135 | 40.5 | 192537 | 58 | 152.5 | 869982 | 152.5 | 869982 | 11 | 52294 | 28.45 | 135251.3 | 193 | 0 | 60 | 4754 | 88 | 4754 | 16 | 0 | 80 | 0 | 275 | 0 | 1114813 | 60891609 | 234.5 | 12808.5
14 | Cantt | RAZA HALL | Urban | 2500 | 97 | 29.1 | 72750 | 53 | 120.9 | 362700 | 120.9 | 362700 | 8 | 20000 | 32.15 | 80375 | 150 | 0 | 60 | 2500 | 88 | 2500 | 16 | 0 | 80 | 0 | 275 | 0 | 455450 | 26802750 | 182.18 | 10721.1
15 | Cantt | NEW NAWAN SHER | Urban | 2464 | 120 | 36 | 88704 | 22 | 106 | 313420.8 | 106 | 313420.8 | 13 | 32032 | 25.4 | 62585.6 | 142 | 0 | 60 | 2464 | 88 | 2464 | 16 | 0 | 80 | 0 | 275 | 0 | 434156.8 | 22826496 | 176.2 | 9264
16 | Cantt | NEW SURAJ MIANI | Urban | 6272 | 118 | 35.4 | 222028.8 | 43 | 125.6 | 945315.84 | 125.6 | 945315.84 | 8 | 50176 | 13.5 | 84672 | 161 | 0 | 60 | 6272 | 88 | 6272 | 16 | 0 | 80 | 0 | 275 | 0 | 1217520.64 | 62465356.8 | 194.12 | 9959.4
17 | Cantt | BOHER GATE | Urban | 6018 | 106 | 31.8 | 191372.4 | 40 | 114.2 | 824706.72 | 114.2 | 824706.72 | 14 | 84252 | 47.3 | 284651.4 | 146 | 0 | 60 | 6018 | 88 | 6018 | 16 | 0 | 80 | 0 | 275 | 0 | 1100331.12 | 67135604.4 | 182.84 | 11155.8
18 | Cantt | HASSAN PARWANA | Urban | 3495 | 101 | 30.3 | 105898.5 | 24 | 94.7 | 397171.8 | 94.7 | 397171.8 | 17 | 59415 | 43.4 | 151683 | 125 | 0 | 60 | 3495 | 88 | 3495 | 16 | 3495 | 80 | 0 | 275 | 0 | 562485.3 | 33248983.5 | 160.94 | 9513.3
19 | Cantt | AKBAR ROAD | Urban | 4049 | 111 | 33.3 | 134831.7 | 33 | 110.7 | 537869.16 | 110.7 | 537869.16 | 20 | 80980 | 60.1 | 243344.9 | 144 | 0 | 60 | 4049 | 88 | 4049 | 16 | 4049 | 80 | 0 | 275 | 0 | 753680.86 | 47277338.7 | 186.14 | 11676.3
20 | Cantt | NUSRAT ROAD | Urban | 1053 | 48 | 14.4 | 15163.2 | 15 | 48.6 | 61410.96 | 48.6 | 61410.96 | 5 | 5265 | 20.5 | 21586.5 | 63 | 0 | 60 | 1053 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 81839.16 | 5025337.2 | 77.72 | 4772.4
21 | Cantt | FAREED ABAD | Urban | 5050 | 46 | 13.8 | 69690 | 5 | 37.2 | 225432 | 37.2 | 225432 | 2 | 10100 | 7 | 35350 | 51 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 305222 | 15855990 | 60.44 | 3139.8
22 | Cantt | RAILWAY ROAD | Urban | 4578 | 109 | 32.7 | 149700.6 | 17 | 93.3 | 512552.88 | 93.3 | 512552.88 | 9 | 41202 | 28.4 | 130015.2 | 126 | 0 | 60 | 4578 | 88 | 4578 | 16 | 0 | 80 | 0 | 275 | 0 | 703455.48 | 39003186.6 | 153.66 | 8519.7
23 | Cantt | KHUDAAD COLONY | Urban | 9953 | 267 | 80.1 | 797235.3 | 17 | 203.9 | 2435300.04 | 203.9 | 2435300.04 | 7 | 69671 | 20 | 199060 | 284 | 0 | 60 | 9953 | 88 | 9953 | 16 | 0 | 80 | 0 | 275 | 0 | 3302206.34 | 160453308.3 | 331.78 | 16121.1
24 | Cantt | I.ESTET-II | Urban | 109 | 157 | 47.1 | 5133.9 | 18 | 127.9 | 16729.32 | 127.9 | 16729.32 | 20 | 2180 | 52 | 5668 | 175 | 0 | 60 | 109 | 88 | 109 | 16 | 109 | 80 | 0 | 275 | 0 | 24043.22 | 1359240.9 | 220.58 | 12470.1
25 | Cantt | INDUSTRIAL ESTAT-1 | Urban | 117 | 174 | 52.2 | 6107.4 | 16 | 137.8 | 19347.12 | 137.8 | 19347.12 | 23 | 2691 | 91 | 10647 | 190 | 0 | 60 | 117 | 88 | 117 | 16 | 117 | 80 | 117 | 275 | 0 | 28145.52 | 1817969.4 | 240.56 | 15538.2
26 | Cantt | NEW FAROOQ PURA | Urban | 9247 | 109 | 32.7 | 302376.9 | 40 | 116.3 | 1290511.32 | 116.3 | 1290511.32 | 28 | 258916 | 64.4 | 595506.8 | 149 | 0 | 60 | 9247 | 88 | 9247 | 16 | 9247 | 80 | 0 | 275 | 0 | 1851804.22 | 114068217.9 | 200.26 | 12335.7
27 | Cantt | FAROOQ PURA | Urban | 5678 | 147 | 44.1 | 250399.8 | 22 | 124.9 | 851018.64 | 124.9 | 851018.64 | 6 | 34068 | 15.1 | 85737.8 | 169 | 0 | 60 | 5678 | 88 | 5678 | 16 | 0 | 80 | 0 | 275 | 0 | 1135486.44 | 56956585.8 | 199.98 | 10031.1
28 | Cantt | CANTT AVENUE | Urban | 50 | 5 | 1.5 | 75 | 3 | 6.5 | 390 | 6.5 | 390 | 4 | 200 | 4 | 200 | 8 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 665 | 35625 | 13.3 | 712.5
29 | Cantt | AL-QURAISH | Urban | 3832 | 131 | 39.3 | 150597.6 | 7 | 98.7 | 453862.08 | 98.7 | 453862.08 | 17 | 65144 | 62.55 | 239691.6 | 138 | 0 | 60 | 3832 | 88 | 3832 | 16 | 3832 | 80 | 0 | 275 | 0 | 669603.68 | 42065013.6 | 174.74 | 10977.3
30 | Cantt | INDUSTRIAL ESTATE-3 | Urban | 91 | 170 | 51 | 4641 | 15 | 134 | 14632.8 | 134 | 14632.8 | 20 | 1820 | 58 | 5278 | 185 | 0 | 60 | 91 | 88 | 91 | 16 | 91 | 80 | 0 | 275 | 0 | 21093.8 | 1208571 | 231.8 | 13281
31 | Cantt | WHITE HOUSE | Urban | 6758 | 134 | 40.2 | 271671.6 | 35 | 128.8 | 1044516.48 | 128.8 | 1044516.48 | 228 | 1540824 | 269 | 1817902 | 169 | 0 | 60 | 6758 | 88 | 6758 | 16 | 6758 | 80 | 6758 | 275 | 0 | 2857012.08 | 172560123.6 | 422.76 | 25534.2
32 | Cantt | PEARL CITY | Urban | 313 | 21 | 6.3 | 1971.9 | 5 | 19.7 | 7399.32 | 19.7 | 7399.32 | 2 | 626 | 10 | 3130 | 26 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 9997.22 | 637674.9 | 31.94 | 2037.3
33 | Cantt | DREAM GARDEN | Urban | 220 | 15 | 4.5 | 990 | 5 | 15.5 | 4092 | 15.5 | 4092 | 2 | 440 | 10 | 2200 | 20 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 5522 | 380490 | 25.1 | 1729.5
34 | Cantt | POWER HOUSE | Urban | 5603 | 54 | 16.2 | 90768.6 | 26 | 63.8 | 428965.68 | 63.8 | 428965.68 | 13 | 72839 | 42 | 235326 | 80 | 0 | 60 | 5603 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 592573.28 | 40129806.6 | 105.76 | 7162.2
35 | Cantt | POWER HOUSE | Urban | 3777 | 94 | 28.2 | 106511.4 | 8 | 73.8 | 334491.12 | 73.8 | 334491.12 | 19 | 71763 | 70.55 | 266467.35 | 102 | 0 | 60 | 3777 | 88 | 3777 | 16 | 3777 | 80 | 0 | 275 | 0 | 512765.52 | 36377042.4 | 135.76 | 9631.2
36 | Cantt | AIR FORCE COLONY | Urban | 38 | 15 | 4.5 | 171 | 10 | 20.5 | 934.8 | 20.5 | 934.8 | 1 | 38 | 6 | 228 | 25 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 1143.8 | 70281 | 30.1 | 1849.5
37 | Cantt | INDUSTRIAL-4 | Urban | 66 | 239 | 71.7 | 4732.2 | 19 | 186.3 | 14754.96 | 186.3 | 14754.96 | 13 | 858 | 50 | 3300 | 258 | 0 | 60 | 66 | 88 | 66 | 16 | 0 | 80 | 0 | 275 | 0 | 20345.16 | 1097494.2 | 308.26 | 16628.7
38 | Cantt | INDUSTRIAL-5 | Urban | 56 | 137 | 41.1 | 2301.6 | 9 | 104.9 | 7049.28 | 104.9 | 7049.28 | 16 | 896 | 67 | 3752 | 146 | 0 | 60 | 56 | 88 | 56 | 16 | 0 | 80 | 0 | 275 | 0 | 10246.88 | 654981.6 | 182.98 | 11696.1
39 | Cantt | PWWB HOUSING COMPLEX | Urban | 996 | 62 | 18.6 | 18525.6 | 3 | 46.4 | 55457.28 | 46.4 | 55457.28 | 10 | 9960 | 38 | 37848 | 65 | 0 | 60 | 996 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 83942.88 | 5653893.6 | 84.28 | 5676.6
40 | Mumtazabad | GHEE MILL | Urban | 6364 | 103 | 30.9 | 196647.6 | 93 | 165.1 | 1260835.68 | 165.1 | 1260835.68 | 6 | 38184 | 28.25 | 179783 | 196 | 0 | 60 | 6364 | 88 | 6364 | 16 | 0 | 80 | 0 | 275 | 0 | 1495667.28 | 87027063.6 | 235.02 | 13674.9
41 | Mumtazabad | KAREEM ABAD | Urban | 5516 | 65 | 19.5 | 107562 | 92 | 137.5 | 910140 | 137.5 | 910140 | 14 | 77224 | 53.45 | 294830.2 | 157 | 0 | 60 | 5516 | 88 | 5516 | 16 | 0 | 80 | 0 | 275 | 0 | 1094926 | 72620898 | 198.5 | 13165.5
42 | Mumtazabad | NEW MUMTAZABAD | Urban | 6048 | 15 | 4.5 | 27216 | 20 | 30.5 | 221356.8 | 30.5 | 221356.8 | 0 | 0 | 0 | 0 | 35 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 248572.8 | 13363056 | 41.1 | 2209.5
43 | Mumtazabad | PEOPLES COLONY | Urban | 10168 | 159 | 47.7 | 485013.6 | 200 | 311.3 | 3798358.08 | 311.3 | 3798358.08 | 7 | 71176 | 24.3 | 247082.4 | 359 | 0 | 60 | 10168 | 88 | 10168 | 16 | 0 | 80 | 0 | 275 | 0 | 4354547.68 | 244181469.6 | 428.26 | 24014.7
44 | Mumtazabad | GHALA MANDI | Urban | 4937 | 100 | 30 | 148110 | 191 | 261 | 1546268.4 | 261 | 1546268.4 | 15 | 74055 | 61.1 | 301650.7 | 291 | 0 | 60 | 4937 | 88 | 4937 | 16 | 0 | 80 | 0 | 275 | 0 | 1768433.4 | 111319476 | 358.2 | 22548
45 | Mumtazabad | NEW RASHID ROAD | Urban | 2453 | 75 | 22.5 | 55192.5 | 41 | 93.5 | 275226.6 | 93.5 | 275226.6 | 10 | 24530 | 41.45 | 101676.85 | 116 | 0 | 60 | 2453 | 88 | 2453 | 16 | 0 | 80 | 0 | 275 | 0 | 354949.1 | 22779784.5 | 144.7 | 9286.5
46 | Mumtazabad | RASHID ROAD | Urban | 5492 | 82 | 24.6 | 135103.2 | 111 | 168.4 | 1109823.36 | 168.4 | 1109823.36 | 10 | 54920 | 30.35 | 166682.2 | 193 | 0 | 60 | 5492 | 88 | 5492 | 16 | 0 | 80 | 0 | 275 | 0 | 1299846.56 | 76995643.2 | 236.68 | 14019.6
47 | Mumtazabad | SHAH SHAMAS | Urban | 2797 | 74 | 22.2 | 62093.4 | 87 | 138.8 | 465868.32 | 138.8 | 465868.32 | 67 | 187399 | 69.55 | 194531.35 | 161 | 0 | 60 | 2797 | 88 | 2797 | 16 | 2797 | 80 | 0 | 275 | 0 | 715360.72 | 39810260.4 | 255.76 | 14233.2
48 | Mumtazabad | ISLAM NAGAR | Urban | 6367 | 120 | 36 | 229212 | 141 | 225 | 1719090 | 225 | 1719090 | 168 | 1069656 | 83.3 | 530371.1 | 261 | 0 | 60 | 6367 | 88 | 6367 | 16 | 6367 | 80 | 6367 | 275 | 0 | 3017958 | 135655302 | 474 | 21306
49 | Mumtazabad | MAKHDOOM RASHID CITY | Urban | 6081 | 316 | 94.8 | 576478.8 | 107 | 328.2 | 2394941.04 | 328.2 | 2394941.04 | 12 | 72972 | 45.4 | 276077.4 | 423 | 0 | 60 | 6081 | 88 | 6081 | 16 | 0 | 80 | 0 | 275 | 0 | 3044391.84 | 161990542.8 | 500.64 | 26638.8
50 | City | NEW HUSSAIN AGHAI | Urban | 6482 | 77 | 23.1 | 149734.2 | 10 | 63.9 | 497039.76 | 63.9 | 497039.76 | 51 | 330582 | 108.3 | 702000.6 | 87 | 0 | 60 | 6482 | 88 | 0 | 16 | 6482 | 80 | 6482 | 275 | 0 | 977355.96 | 72391624.2 | 150.78 | 11168.1
51 | City | HUSSAIN AGAHI | Urban | 5058 | 87 | 26.1 | 132013.8 | 50 | 110.9 | 673118.64 | 110.9 | 673118.64 | 146 | 738468 | 218.35 | 1104414.3 | 137 | 0 | 60 | 5058 | 88 | 5058 | 16 | 5058 | 80 | 5058 | 275 | 0 | 1543600.44 | 107048017.8 | 305.18 | 21164.1
52 | City | CITY | Urban | 7092 | 130 | 39 | 276588 | 27 | 118 | 1004227.2 | 118 | 1004227.2 | 60 | 425520 | 122.31 | 867422.52 | 157 | 0 | 60 | 7092 | 88 | 7092 | 16 | 7092 | 80 | 7092 | 275 | 0 | 1706335.2 | 113128747.2 | 240.6 | 15951.6
53 | City | ISHFAQ HAMEED SHAHEED | Urban | 5482 | 16 | 4.8 | 26313.6 | 11 | 22.2 | 146040.48 | 22.2 | 146040.48 | 5 | 27410 | 22 | 120604 | 27 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 199764.08 | 16077609.6 | 36.44 | 2932.8
54 | City | LIAQAT ABAD | Urban | 6262 | 95 | 28.5 | 178467 | 16 | 82.5 | 619938 | 82.5 | 619938 | 7 | 43834 | 23.1 | 144652.2 | 111 | 0 | 60 | 6262 | 88 | 6262 | 16 | 0 | 80 | 0 | 275 | 0 | 842239 | 46410813 | 134.5 | 7411.5
55 | City | SURAJ KUND ROAD | Urban | 3375 | 87 | 26.1 | 88087.5 | 83 | 143.9 | 582795 | 143.9 | 582795 | 26 | 87750 | 119.48 | 403245 | 170 | 0 | 60 | 3375 | 88 | 3375 | 16 | 3375 | 80 | 3375 | 275 | 0 | 758632.5 | 59426662.5 | 224.78 | 17607.9
56 | City | TIMBER MARKT | Urban | 5758 | 108 | 32.4 | 186559.2 | 38 | 113.6 | 784930.56 | 113.6 | 784930.56 | 7 | 40306 | 8 | 46064 | 146 | 0 | 60 | 5758 | 88 | 5758 | 16 | 0 | 80 | 0 | 275 | 0 | 1011795.76 | 50419351.2 | 175.72 | 8756.4
57 | City | AL-JILAN | Urban | 7443 | 37 | 11.1 | 82617.3 | 25 | 50.9 | 454618.44 | 50.9 | 454618.44 | 12 | 89316 | 2 | 14886 | 62 | 0 | 60 | 7443 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 626551.74 | 28418118.3 | 84.18 | 3818.1
58 | City | SULTAN PURA | Urban | 7721 | 128 | 38.4 | 296486.4 | 87 | 176.6 | 1636234.32 | 176.6 | 1636234.32 | 17 | 131257 | 76.5 | 590656.5 | 215 | 0 | 60 | 7721 | 88 | 7721 | 16 | 7721 | 80 | 0 | 275 | 0 | 2063977.72 | 134502908.4 | 267.32 | 17420.4
59 | City | OLD SHUJAABAD ROAD | Urban | 5101 | 60 | 18 | 91818 | 37 | 79 | 483574.8 | 79 | 483574.8 | 19 | 96919 | 44 | 224444 | 97 | 0 | 60 | 5101 | 88 | 5101 | 16 | 5101 | 80 | 0 | 275 | 0 | 672311.8 | 42756582 | 131.8 | 8382
60 | City | WILLAYAT ABAD | Urban | 4356 | 76 | 22.8 | 99316.8 | 10 | 63.2 | 330359.04 | 63.2 | 330359.04 | 11 | 47916 | 35.3 | 153766.8 | 86 | 0 | 60 | 4356 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 477591.84 | 29345500.8 | 109.64 | 6736.8
61 | City | IQBAL NAGAR | Urban | 3540 | 69 | 20.7 | 73278 | 6 | 54.3 | 230666.4 | 54.3 | 230666.4 | 51 | 180540 | 93.29 | 330246.6 | 75 | 0 | 60 | 3540 | 88 | 0 | 16 | 3540 | 80 | 3540 | 275 | 0 | 484484.4 | 33874614 | 136.86 | 9569.1
62 | City | ARIF PURA | Urban | 5003 | 72 | 21.6 | 108064.8 | 14 | 64.4 | 386631.84 | 64.4 | 386631.84 | 54 | 270162 | 89.01 | 445317.03 | 86 | 0 | 60 | 5003 | 88 | 0 | 16 | 5003 | 80 | 5003 | 275 | 0 | 764858.64 | 50241126.6 | 152.88 | 10042.2
63 | City | TAHIR MAJEED SHAHEED | Urban | 4944 | 44 | 13.2 | 65260.8 | 6 | 36.8 | 218327.04 | 36.8 | 218327.04 | 31 | 153264 | 70.27 | 347414.88 | 50 | 0 | 60 | 0 | 88 | 0 | 16 | 4944 | 80 | 0 | 275 | 0 | 436851.84 | 34140297.6 | 88.36 | 6905.4
64 | City | NISHAT ROAD | Urban | 10721 | 173 | 51.9 | 556419.9 | 129 | 250.1 | 3217586.52 | 250.1 | 3217586.52 | 17 | 182257 | 138.3 | 1482714.3 | 302 | 0 | 60 | 10721 | 88 | 10721 | 16 | 10721 | 80 | 10721 | 275 | 0 | 3956263.42 | 283687308.9 | 369.02 | 26460.9
65 | City | MUZAFFAR ABAD | Urban | 11702 | 263 | 78.9 | 923287.8 | 19 | 203.1 | 2852011.44 | 203.1 | 2852011.44 | 31 | 362762 | 110.55 | 1293656.1 | 282 | 0 | 60 | 11702 | 88 | 11702 | 16 | 11702 | 80 | 11702 | 275 | 0 | 4138061.24 | 251509915.8 | 353.62 | 21492.9
66 | City | CLASSIC VILLAS | Urban | 163 | 36 | 10.8 | 1760.4 | 12 | 37.2 | 7276.32 | 37.2 | 7276.32 | 26 | 4238 | 50.4 | 8215.2 | 48 | 0 | 60 | 0 | 88 | 0 | 16 | 163 | 80 | 0 | 275 | 0 | 13274.72 | 934772.4 | 81.44 | 5734.8
67 | City | GARDEN TOWN | Urban | 5365 | 214 | 64.2 | 344433 | 20 | 169.8 | 1093172.4 | 169.8 | 1093172.4 | 26 | 139490 | 90.55 | 485800.75 | 234 | 0 | 60 | 5365 | 88 | 5365 | 16 | 5365 | 80 | 5365 | 275 | 0 | 1577095.4 | 95771688 | 293.96 | 17851.2
68 | Shujabad | SADAR-UD-DIN SHAH | Urban | 9754 | 309 | 92.7 | 904195.8 | 43 | 259.3 | 3035054.64 | 259.3 | 3035054.64 | 307 | 2994478 | 34 | 331636 | 352 | 0 | 60 | 9754 | 88 | 9754 | 16 | 9754 | 80 | 0 | 275 | 0 | 6933728.44 | 204714025.8 | 710.86 | 20987.7
69 | Shujabad | CITY | Urban | 7591 | 316 | 94.8 | 719626.8 | 44 | 265.2 | 2415759.84 | 265.2 | 2415759.84 | 34 | 258094 | 57 | 432687 | 360 | 0 | 60 | 7591 | 88 | 7591 | 16 | 7591 | 80 | 0 | 275 | 0 | 3393480.64 | 173065690.8 | 447.04 | 22798.8
70 | Shujabad | NORAJA BHUTTA | Urban | 4695 | 435 | 130.5 | 612697.5 | 73 | 377.5 | 2126835 | 377.5 | 2126835 | 139 | 652605 | 330.05 | 1549584.75 | 508 | 0 | 60 | 4695 | 88 | 4695 | 16 | 4695 | 80 | 4695 | 275 | 0 | 3392137.5 | 222423277.5 | 722.5 | 47374.5
71 | Shujabad | CITY JALAL PUR | Urban | 15756 | 310 | 93 | 1465308 | 78 | 295 | 5577624 | 295 | 5577624 | 68 | 1071408 | 260.25 | 4100499 | 388 | 0 | 60 | 15756 | 88 | 15756 | 16 | 15756 | 80 | 15756 | 275 | 0 | 8114340 | 585083304 | 515 | 37134
72 | B.Z (Musa Pak) | SABZA ZAR | Urban | 1991 | 126 | 37.8 | 75259.8 | 53 | 141.2 | 337355.04 | 141.2 | 337355.04 | 8 | 15928 | 17 | 33847 | 179 | 0 | 60 | 1991 | 88 | 1991 | 16 | 0 | 80 | 0 | 275 | 0 | 428542.84 | 22497901.8 | 215.24 | 11299.8
73 | B.Z (Musa Pak) | SHALIMAR | Urban | 7235 | 123 | 36.9 | 266971.5 | 48 | 134.1 | 1164256.2 | 134.1 | 1164256.2 | 6 | 43410 | 21 | 151935 | 171 | 0 | 60 | 7235 | 88 | 7235 | 16 | 0 | 80 | 0 | 275 | 0 | 1474637.7 | 79772386.5 | 203.82 | 11025.9
74 | B.Z (Musa Pak) | USMAN ABAD | Urban | 3819 | 97 | 29.1 | 111132.9 | 48 | 115.9 | 531146.52 | 115.9 | 531146.52 | 8 | 30552 | 1.4618 | 5582.6354 | 145 | 0 | 60 | 3819 | 88 | 3819 | 16 | 0 | 80 | 0 | 275 | 0 | 672831.42 | 32537148.025 | 176.18 | 8519.8083
75 | B.Z (Musa Pak) | GARRAY WALA | Urban | 8495 | 94 | 28.2 | 239559 | 23 | 88.8 | 905227.2 | 88.8 | 905227.2 | 5 | 42475 | 20 | 169900 | 117 | 0 | 60 | 8495 | 88 | 8495 | 16 | 0 | 80 | 0 | 275 | 0 | 1187261.2 | 65226309 | 139.76 | 7678.2
76 | B.Z (Musa Pak) | KHAN VILLAGE ROAD | Urban | 5569 | 74 | 22.2 | 123631.8 | 20 | 71.8 | 479825.04 | 71.8 | 479825.04 | 6 | 33414 | 24 | 133656 | 94 | 0 | 60 | 5569 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 636870.84 | 37179757.8 | 114.36 | 6676.2
77 | B.Z (Musa Pak) | NAWAB PUR ROAD | Urban | 9754 | 144 | 43.2 | 421372.8 | 34 | 134.8 | 1577807.04 | 134.8 | 1577807.04 | 8 | 78032 | 33 | 321882 | 178 | 0 | 60 | 9754 | 88 | 9754 | 16 | 0 | 80 | 0 | 275 | 0 | 2077211.84 | 115245460.8 | 212.96 | 11815.2
78 | B.Z (Musa Pak) | WAINS | Urban | 6130 | 147 | 44.1 | 270333 | 86 | 188.9 | 1389548.4 | 188.9 | 1389548.4 | 28 | 171640 | 83.05 | 509096.5 | 233 | 0 | 60 | 6130 | 88 | 6130 | 16 | 6130 | 80 | 6130 | 275 | 0 | 1831521.4 | 114729693 | 298.78 | 18716.1
79 | B.Z (Musa Pak) | GULGASHT COLONY | Urban | 5586 | 80 | 24 | 134064 | 25 | 81 | 542959.2 | 81 | 542959.2 | 5 | 27930 | 22 | 122892 | 105 | 0 | 60 | 5586 | 88 | 5586 | 16 | 0 | 80 | 0 | 275 | 0 | 704953.2 | 40353264 | 126.2 | 7224
80 | B.Z (Musa Pak) | PIR KHURSHID COLONY | Urban | 7050 | 102 | 30.6 | 215730 | 40 | 111.4 | 942444 | 111.4 | 942444 | 18 | 126900 | 23 | 162150 | 142 | 0 | 60 | 7050 | 88 | 7050 | 16 | 7050 | 80 | 0 | 275 | 0 | 1285074 | 66922830 | 182.28 | 9492.6
81 | B.Z (Musa Pak) | SHAMAS ABAD | Urban | 7003 | 97 | 29.1 | 203787.3 | 74 | 141.9 | 1192470.84 | 141.9 | 1192470.84 | 40 | 280120 | 61 | 427183 | 171 | 0 | 60 | 7003 | 88 | 7003 | 16 | 7003 | 80 | 0 | 275 | 0 | 1676378.14 | 97790592.3 | 239.38 | 13964.1
82 | B.Z (Musa Pak) | EID GAH ROAD | Urban | 7132 | 178 | 53.4 | 380848.8 | 94 | 218.6 | 1870866.24 | 218.6 | 1870866.24 | 8 | 57056 | 20 | 142640 | 272 | 0 | 60 | 7132 | 88 | 7132 | 16 | 0 | 80 | 0 | 275 | 0 | 2308771.04 | 121952920.8 | 323.72 | 17099.4
83 | B.Z (Musa Pak) | HAZOORI BAGH | Urban | 4656 | 96 | 28.8 | 134092.8 | 51 | 118.2 | 660407.04 | 118.2 | 660407.04 | 8 | 37248 | 21 | 97776 | 147 | 0 | 60 | 4656 | 88 | 4656 | 16 | 0 | 80 | 0 | 275 | 0 | 831747.84 | 45893260.8 | 178.64 | 9856.8
84 | B.Z (Musa Pak) | OFFICER COLONY | Urban | 2147 | 90 | 27 | 57969 | 48 | 111 | 285980.4 | 111 | 285980.4 | 11 | 23617 | 40 | 85880 | 138 | 0 | 60 | 2147 | 88 | 2147 | 16 | 0 | 80 | 0 | 275 | 0 | 367566.4 | 22485531 | 171.2 | 10473
85 | B.Z (Musa Pak) | AHMAD | Urban | 10971 | 132 | 39.6 | 434451.6 | 113 | 205.4 | 2704132.08 | 205.4 | 2704132.08 | 24 | 263304 | 79 | 866709 | 245 | 0 | 60 | 10971 | 88 | 10971 | 16 | 10971 | 80 | 0 | 275 | 0 | 3401887.68 | 215553819.6 | 310.08 | 19647.6
86 | B.Z (Musa Pak) | MASOOM SHAH | Urban | 3488 | 178 | 53.4 | 186259.2 | 25 | 149.6 | 626165.76 | 149.6 | 626165.76 | 17 | 59296 | 70.55 | 246078.4 | 203 | 0 | 60 | 3488 | 88 | 3488 | 16 | 3488 | 80 | 0 | 275 | 0 | 871720.96 | 52893427.2 | 249.92 | 15164.4
87 | B.Z (Musa Pak) | ROYAL ORCHARD-I | Urban | 345 | 48 | 14.4 | 4968 | 30 | 63.6 | 26330.4 | 63.6 | 26330.4 | 22 | 7590 | 94 | 32430 | 78 | 0 | 60 | 345 | 88 | 0 | 16 | 345 | 80 | 345 | 275 | 0 | 38888.4 | 3540528 | 112.72 | 10262.4
88 | B.Z (Musa Pak) | WAHDAT COLONY | Urban | 5376 | 99 | 29.7 | 159667.2 | 48 | 117.3 | 756725.76 | 117.3 | 756725.76 | 17 | 91392 | 31 | 166656 | 147 | 0 | 60 | 5376 | 88 | 5376 | 16 | 5376 | 80 | 0 | 275 | 0 | 1007784.96 | 55881907.2 | 187.46 | 10394.7
89 | B.Z (Musa Pak) | JAHANGIR ABAD | Urban | 6363 | 345 | 103.5 | 658570.5 | 149 | 390.5 | 2981701.8 | 390.5 | 2981701.8 | 39 | 248157 | 159 | 1011717 | 494 | 0 | 60 | 6363 | 88 | 6363 | 16 | 6363 | 80 | 6363 | 275 | 0 | 3888429.3 | 241580839.5 | 611.1 | 37966.5
90 | B.Z (Musa Pak) | PGHSF-3 | Urban | 18 | 35 | 10.5 | 189 | 14 | 38.5 | 831.6 | 38.5 | 831.6 | 5 | 90 | 19 | 342 | 49 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 1110.6 | 70983 | 61.7 | 3943.5
91 | B.Z (Musa Pak) | AL-FALAH MODERN CITY | Urban | 23 | 15 | 4.5 | 103.5 | 11 | 21.5 | 593.4 | 21.5 | 593.4 | 13 | 299 | 56 | 1288 | 26 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 995.9 | 113194.5 | 43.3 | 4921.5
92 | B.Z (Musa Pak) | PGHSF-1 | Urban | 12 | 25 | 7.5 | 90 | 16 | 33.5 | 482.4 | 33.5 | 482.4 | 68 | 816 | 86 | 1032 | 41 | 0 | 60 | 0 | 88 | 0 | 16 | 12 | 80 | 12 | 275 | 0 | 1388.4 | 91134 | 115.7 | 7594.5
93 | B.Z (Musa Pak) | WAPDA COLONY | Urban | 2252 | 47 | 14.1 | 31753.2 | 30 | 62.9 | 169980.96 | 62.9 | 169980.96 | 4 | 9008 | 17 | 38284 | 77 | 0 | 60 | 2252 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 210742.16 | 12591157.2 | 93.58 | 5591.1
94 | B.Z (Musa Pak) | ROYAL ORCHARD-II | Urban | 79 | 19 | 5.7 | 450.3 | 25 | 38.3 | 3630.84 | 38.3 | 3630.84 | 13 | 1027 | 57 | 4503 | 44 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 5108.14 | 489381.3 | 64.66 | 6194.7
95 | B.Z (Musa Pak) | PGHSF-4 | Urban | 91 | 31 | 9.3 | 846.3 | 19 | 40.7 | 4444.44 | 40.7 | 4444.44 | 5 | 455 | 19 | 1729 | 50 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 5745.74 | 372945.3 | 63.14 | 4098.3
96 | B.Z (Musa Pak) | TARIQ ABAD | Urban | 7808 | 107 | 32.1 | 250636.8 | 55 | 129.9 | 1217111.04 | 129.9 | 1217111.04 | 8 | 62464 | 20 | 156160 | 162 | 0 | 60 | 7808 | 88 | 7808 | 16 | 0 | 80 | 0 | 275 | 0 | 1530211.84 | 83148172.8 | 195.98 | 10649.1
97 | B.Z (Musa Pak) | NAQSHBAND | Urban | 4981 | 100 | 30 | 149430 | 66 | 136 | 812899.2 | 136 | 812899.2 | 5 | 24905 | 20 | 99620 | 166 | 0 | 60 | 4981 | 88 | 4981 | 16 | 0 | 80 | 0 | 275 | 0 | 987234.2 | 55199442 | 198.2 | 11082
98 | B.Z (Musa Pak) | JUDICIAL COMPLEX | Urban | 91 | 13 | 3.9 | 354.9 | 4 | 13.1 | 1430.52 | 13.1 | 1430.52 | 1 | 91 | 20.8 | 1892.8 | 17 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 1876.42 | 200463.9 | 20.62 | 2202.9
99 | B.Z (Musa Pak) | DHA | Urban | 115 | 16 | 4.8 | 552 | 3 | 14.2 | 1959.6 | 14.2 | 1959.6 | 26 | 2990 | 111.54 | 12827.1 | 19 | 0 | 60 | 0 | 88 | 0 | 16 | 115 | 80 | 115 | 275 | 0 | 5501.6 | 888858 | 47.84 | 7729.2
100 | B.Z (Musa Pak) | BUTCH VILLAS | Urban | 3648 | 205 | 61.5 | 224352 | 106 | 249.5 | 1092211.2 | 249.5 | 1092211.2 | 53 | 193344 | 171.15 | 624355.2 | 311 | 0 | 60 | 3648 | 88 | 3648 | 16 | 3648 | 80 | 3648 | 275 | 0 | 1509907.2 | 103667040 | 413.9 | 28417.5
101 | B.Z (Musa Pak) | BUCH VILLAS-2 | Urban | 69 | 19 | 5.7 | 393.3 | 11 | 24.3 | 2012.04 | 24.3 | 2012.04 | 27 | 1863 | 115.39 | 7961.91 | 30 | 0 | 60 | 0 | 88 | 0 | 16 | 69 | 80 | 69 | 275 | 0 | 4268.34 | 599616.9 | 61.86 | 8690.1
102 | B.Z (Musa Pak) | BUCH VILLAS-1 | Urban | 1199 | 25 | 7.5 | 8992.5 | 8 | 25.5 | 36689.4 | 25.5 | 36689.4 | 27 | 32373 | 115.39 | 138352.61 | 33 | 0 | 60 | 0 | 88 | 0 | 16 | 1199 | 80 | 1199 | 275 | 0 | 78054.9 | 10529498.1 | 65.1 | 8781.9
103 | B.Z (Musa Pak) | MODEL TOWN | Urban | 3671 | 141 | 42.3 | 155283.3 | 46 | 144.7 | 637432.44 | 144.7 | 637432.44 | 31 | 113801 | 91.17 | 334685.07 | 187 | 0 | 60 | 3671 | 88 | 3671 | 16 | 3671 | 80 | 3671 | 275 | 0 | 906516.74 | 58792900.5 | 246.94 | 16015.5
104 | B.Z (Musa Pak) | WAPDA TOWN | Urban | 3555 | 146 | 43.8 | 155709 | 97 | 199.2 | 849787.2 | 199.2 | 849787.2 | 25 | 88875 | 96.3 | 342346.5 | 243 | 0 | 60 | 3555 | 88 | 3555 | 16 | 3555 | 80 | 3555 | 275 | 0 | 1094371.2 | 71995149 | 307.84 | 20251.8
105 | B.Z (Musa Pak) | MDA COLONY | Urban | 2326 | 130 | 39 | 90714 | 113 | 204 | 569404.8 | 204 | 569404.8 | 29 | 67454 | 76.2 | 177241.2 | 243 | 0 | 60 | 2326 | 88 | 2326 | 16 | 2326 | 80 | 0 | 275 | 0 | 727572.8 | 45070902 | 312.8 | 19377
106 | S.R.Alam | JINNAH CHOWK | Urban | 4444 | 145 | 43.5 | 193314 | 19 | 120.5 | 642602.4 | 120.5 | 642602.4 | 18 | 79992 | 74.05 | 329078.2 | 164 | 0 | 60 | 4444 | 88 | 4444 | 16 | 4444 | 80 | 0 | 275 | 0 | 915908.4 | 58880778 | 206.1 | 13249.5
107 | S.R.Alam | AL-HALAL | Urban | 6587 | 476 | 142.8 | 940623.6 | 59 | 392.2 | 3100105.68 | 392.2 | 3100105.68 | 21 | 138327 | 78.35 | 516091.45 | 535 | 0 | 60 | 6587 | 88 | 6587 | 16 | 6587 | 80 | 0 | 275 | 0 | 4179056.28 | 219793698.6 | 634.44 | 33367.8
108 | S.R.Alam | GHOUS PURA | Urban | 4696 | 129 | 38.7 | 181735.2 | 5 | 95.3 | 537034.56 | 95.3 | 537034.56 | 19 | 89224 | 82.05 | 385306.8 | 134 | 0 | 60 | 4696 | 88 | 4696 | 16 | 4696 | 80 | 4696 | 275 | 0 | 807993.76 | 55885687.2 | 172.06 | 11900.7
109 | S.R.Alam | FATIMA JINNAH COLONY | Urban | 993 | 266 | 79.8 | 79241.4 | 17 | 203.2 | 242133.12 | 203.2 | 242133.12 | 8 | 7944 | 32.5 | 32272.5 | 283 | 0 | 60 | 993 | 88 | 993 | 16 | 0 | 80 | 0 | 275 | 0 | 329318.52 | 16702061.4 | 331.64 | 16819.8
110 | S.R.Alam | GULSHAN MARKET | Urban | 4027 | 92 | 27.6 | 111145.2 | 23 | 87.4 | 422351.76 | 87.4 | 422351.76 | 196 | 789292 | 256.35 | 1032321.45 | 115 | 0 | 60 | 4027 | 88 | 4027 | 16 | 4027 | 80 | 4027 | 275 | 0 | 1322788.96 | 87613828.2 | 328.48 | 21756.6
111 | S.R.Alam | S/RUKAN-E-ALAM | Urban | 5073 | 82 | 24.6 | 124795.8 | 22 | 79.4 | 483355.44 | 79.4 | 483355.44 | 19 | 96387 | 72.15 | 366016.95 | 104 | 0 | 60 | 5073 | 88 | 5073 | 16 | 5073 | 80 | 0 | 275 | 0 | 704538.24 | 51336730.8 | 138.88 | 10119.6
112 | S.R.Alam | D-MARKET | Urban | 2515 | 81 | 24.3 | 61114.5 | 6 | 62.7 | 189228.6 | 62.7 | 189228.6 | 21 | 52815 | 81.5 | 204972.5 | 87 | 0 | 60 | 2515 | 88 | 0 | 16 | 2515 | 80 | 2515 | 275 | 0 | 303158.1 | 23835409.5 | 120.54 | 9477.3
113 | S.R.Alam | GHAFOOR | Urban | 10788 | 121 | 36.3 | 391604.4 | 100 | 184.7 | 2391052.32 | 184.7 | 2391052.32 | 20 | 215760 | 57.25 | 617613 | 221 | 0 | 60 | 10788 | 88 | 10788 | 16 | 10788 | 80 | 0 | 275 | 0 | 2998416.72 | 181694732.4 | 277.94 | 16842.3
114 | S.R.Alam | ALI TOWN | Urban | 3647 | 100 | 30 | 109410 | 13 | 83 | 363241.2 | 83 | 363241.2 | 21 | 76587 | 72.35 | 263860.45 | 113 | 0 | 60 | 3647 | 88 | 3647 | 16 | 3647 | 80 | 0 | 275 | 0 | 549238.2 | 37954329 | 150.6 | 10407
115 | S.R.Alam | USMAN E GHANI ROAD | Urban | 8087 | 114 | 34.2 | 276575.4 | 14 | 93.8 | 910272.72 | 93.8 | 910272.72 | 19 | 153653 | 79.25 | 640894.75 | 128 | 0 | 60 | 8087 | 88 | 8087 | 16 | 8087 | 80 | 0 | 275 | 0 | 1340501.12 | 93899774.4 | 165.76 | 11611.2
116 | S.R.Alam | NEW MULTAN | Urban | 4896 | 133 | 39.9 | 195350.4 | 16 | 109.1 | 640984.32 | 109.1 | 640984.32 | 21 | 102816 | 80 | 391680 | 149 | 1 | 60 | 4896 | 88 | 4896 | 16 | 4896 | 80 | 0 | 275 | 0 | 939150.72 | 62545910.4 | 191.82 | 12774.9
117 | S.R.Alam | SAMIJABAD | Urban | 6719 | 183 | 54.9 | 368873.1 | 8 | 136.1 | 1097347.08 | 136.1 | 1097347.08 | 85 | 571115 | 159.51 | 1071747.69 | 191 | 2 | 60 | 6719 | 88 | 6719 | 16 | 6719 | 80 | 6719 | 275 | 0 | 2037335.18 | 131252305.5 | 303.22 | 19534.5
118 | S.R.Alam | NEW HAFIZ JAMAL | Urban | 8176 | 159 | 47.7 | 389995.2 | 13 | 124.3 | 1219532.16 | 124.3 | 1219532.16 | 62 | 506912 | 90.3 | 738292.8 | 172 | 3 | 60 | 8176 | 88 | 8176 | 16 | 8176 | 80 | 8176 | 275 | 0 | 2116439.36 | 118639483.2 | 258.86 | 14510.7
119 | S.R.Alam | MANZOOR ABAD | Urban | 6022 | 95 | 28.5 | 171627 | 14 | 80.5 | 581725.2 | 80.5 | 581725.2 | 66 | 397452 | 110.37 | 664648.14 | 109 | 4 | 60 | 6022 | 88 | 6022 | 16 | 6022 | 80 | 6022 | 275 | 0 | 1150804.2 | 75297281.4 | 191.1 | 12503.7
120 | S.R.Alam | MANZOOR ABAD | Urban | 3926 | 32 | 9.6 | 37689.6 | 36 | 58.4 | 275134.08 | 58.4 | 275134.08 | 10 | 39260 | 17.14 | 67291.64 | 68 | 5 | 60 | 3926 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 352083.68 | 20658612 | 89.68 | 5262
121 | S.R.Alam | NEW VEHARI RD | Urban | 10970 | 604 | 181.2 | 1987764 | 54 | 476.8 | 6276595.2 | 476.8 | 6276595.2 | 20 | 219400 | 168.55 | 1848993.5 | 658 | 6 | 60 | 10970 | 88 | 10970 | 16 | 10970 | 80 | 10970 | 275 | 0 | 8483759.2 | 493498614 | 773.36 | 44986.2
122 | S.R.Alam | HAFIZ JAMAL | Urban | 5020 | 156 | 46.8 | 234936 | 9 | 118.2 | 712036.8 | 118.2 | 712036.8 | 13 | 65260 | 47.35 | 237697 | 165 | 7 | 60 | 5020 | 88 | 5020 | 16 | 0 | 80 | 0 | 275 | 0 | 1012232.8 | 57688836 | 201.64 | 11491.8
123 | S.R.Alam | DEHLI GATE | Urban | 6839 | 72 | 21.6 | 147722.4 | 6 | 56.4 | 462863.52 | 56.4 | 462863.52 | 62 | 424018 | 108.34 | 740937.26 | 78 | 8 | 60 | 6839 | 88 | 0 | 16 | 6839 | 80 | 6839 | 275 | 0 | 1034603.92 | 72671214 | 151.28 | 10626
124 | S.R.Alam | SHARIF PURA | Urban | 2214 | 103 | 30.9 | 68412.6 | 10 | 82.1 | 218123.28 | 82.1 | 218123.28 | 10 | 22140 | 39.1 | 86567.4 | 113 | 9 | 60 | 2214 | 88 | 2214 | 16 | 0 | 80 | 0 | 275 | 0 | 308675.88 | 18486678.6 | 139.42 | 8349.9
125 | S.R.Alam | GULBERG CLNY | Urban | 4136 | 78 | 23.4 | 96782.4 | 101 | 155.6 | 772273.92 | 155.6 | 772273.92 | 55 | 227480 | 67.3 | 278352.8 | 179 | 10 | 60 | 4136 | 88 | 4136 | 16 | 4136 | 80 | 0 | 275 | 0 | 1096536.32 | 63327950.4 | 265.12 | 15311.4
126 | S.R.Alam | MUSLIM TOWN | Urban | 6704 | 172 | 51.6 | 345926.4 | 17 | 137.4 | 1105355.52 | 137.4 | 1105355.52 | 18 | 120672 | 58.35 | 391178.4 | 189 | 11 | 60 | 6704 | 88 | 6704 | 16 | 6704 | 80 | 0 | 275 | 0 | 1571953.92 | 90829814.4 | 234.48 | 13548.6
127 | S.R.Alam | ANSAR COLONY | Urban | 6516 | 133 | 39.9 | 259988.4 | 18 | 111.1 | 868713.12 | 111.1 | 868713.12 | 9 | 58644 | 35.1 | 228711.6 | 151 | 12 | 60 | 6516 | 88 | 6516 | 16 | 0 | 80 | 0 | 275 | 0 | 1187345.52 | 66625448.4 | 182.22 | 10224.9
128 | S.R.Alam | DEHLI GATE | Urban | 6442 | 108 | 32.4 | 208720.8 | 13 | 88.6 | 684913.44 | 88.6 | 684913.44 | 143 | 921206 | 32.5 | 209365 | 121 | 13 | 60 | 6442 | 88 | 6442 | 16 | 6442 | 80 | 0 | 275 | 0 | 1814840.24 | 54282868.8 | 281.72 | 8426.4
129 | S.R.Alam | CHAWAN COLONY | Urban | 8680 | 46 | 13.8 | 119784 | 14 | 46.2 | 481219.2 | 46.2 | 481219.2 | 12 | 104160 | 17.55 | 152334 | 60 | 14 | 60 | 8680 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 705163.2 | 38372544 | 81.24 | 4420.8
130 | B.Z(musa pak) | DHA M-1 | urban | 4 | 4 | 1.2 | 4.8 | 1 | 3.8 | 18.24 | 3.8 | 18.24 | 0 | 0 | 0 | 0 | 5 | 15 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 23.04 | 1108.8 | 5.76 | 277.2
131 | B.Z(musa pak) | PGHSF-2 | urban | 3 | 25 | 7.5 | 22.5 | 15 | 32.5 | 117 | 32.5 | 117 | 7 | 21 | 22 | 66 | 40 | 16 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 160.5 | 11047.5 | 53.5 | 3682.5
132 | B.Z(musa pak) | Farooq Azam | urban | 2 | 117 | 35.1 | 70.2 | 73 | 154.9 | 371.76 | 154.9 | 371.76 | 29 | 58 | 125.19 | 250.38 | 190 | 17 | 60 | 2 | 88 | 2 | 16 | 2 | 80 | 2 | 275 | 0 | 499.96 | 37539 | 249.98 | 18769.5
133 | B.Z(musa pak) | Siddique Abad | urban | 4 | 77 | 23.1 | 92.4 | 8 | 61.9 | 297.12 | 61.9 | 297.12 | 9 | 36 | 40.33 | 161.32 | 85 | 18 | 60 | 4 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 425.52 | 27783.6 | 106.38 | 6945.9
|  | TOTAL |  | 612214 | 15867 | 4760.1 | 26822397.9 | 5135 | 16241.9 | 110142792.12 | 16241.9 | 110142792.12 | 3751 | 20974934 | 8333.9118 | 42840720.7954 | 21002 | 171 | 60 | 582122 | 88 | 517516 | 16 | 333210 | 80 | 173521 | 275 | 0 | 157940124.02 | 9259477968.625 | 257.9819 | 15124.5773

## 400-220 (Urban) D G Khan
Statement of 400/220 V MEPCO Consumers For 2020-21
D.G Khan Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | DG Khan | College Road | Urban | 5026 | 158 | 47.4 | 238232.4 | 39 | 149.6 | 902267.52 | 149.6 | 902267.52 | 42 | 211092 | 79 | 397054 | 197 | 0 | 60 | 5026 | 88 | 5026 | 16 | 5026 | 80 | 0 | 275 | 0 | 1351591.92 | 78673988.4 | 268.92 | 15653.4
2 | DG Khan | Eid Gah Road | Urban | 7833 | 55 | 16.5 | 129244.5 | 38 | 76.5 | 719069.4 | 76.5 | 719069.4 | 27 | 211491 | 61 | 477813 | 93 | 0 | 60 | 7833 | 88 | 7833 | 16 | 7833 | 80 | 0 | 275 | 0 | 1059804.9 | 72200677.5 | 135.3 | 9217.5
3 | DG Khan | New College Road | Urban | 5026 | 150 | 45 | 226170 | 69 | 174 | 1049428.8 | 174 | 1049428.8 | 34 | 170884 | 228 | 1145928 | 219 | 0 | 60 | 5026 | 88 | 5026 | 16 | 5026 | 80 | 5026 | 275 | 0 | 1446482.8 | 132399918 | 287.8 | 26343
4 | DG Khan | Norang Abad | Urban | 7885 | 124 | 37.2 | 293322 | 54 | 140.8 | 1332249.6 | 140.8 | 1332249.6 | 23 | 181355 | 71 | 559835 | 178 | 0 | 60 | 7885 | 88 | 7885 | 16 | 7885 | 80 | 0 | 275 | 0 | 1806926.6 | 114405042 | 229.16 | 14509.2
5 | DG Khan | Khayaban-e-Serwar | Urban | 4979 | 131 | 39.3 | 195674.7 | 47 | 138.7 | 828704.76 | 138.7 | 828704.76 | 40 | 199160 | 125 | 622375 | 178 | 0 | 60 | 4979 | 88 | 4979 | 16 | 4979 | 80 | 4979 | 275 | 0 | 1223539.46 | 87651809.7 | 245.74 | 17604.3
6 | DG Khan | Multan Road | Urban | 5967 | 260 | 78 | 465426 | 46 | 228 | 1632571.2 | 228 | 1632571.2 | 45 | 268515 | 114 | 680238 | 306 | 0 | 60 | 5967 | 88 | 5967 | 16 | 5967 | 80 | 5967 | 275 | 0 | 2366512.2 | 140164830 | 396.6 | 23490
7 | DG Khan | Hospital Road-I | Urban | 4291 | 194 | 58.2 | 249736.2 | 50 | 185.8 | 956721.36 | 185.8 | 956721.36 | 50 | 214550 | 127 | 544957 | 244 | 0 | 60 | 4291 | 88 | 4291 | 16 | 4291 | 80 | 4291 | 275 | 0 | 1421007.56 | 90849910.2 | 331.16 | 21172.2
8 | DG Khan | Hospital Road-II | Urban | 3523 | 42 | 12.6 | 44389.8 | 33 | 62.4 | 263802.24 | 62.4 | 263802.24 | 25 | 88075 | 62 | 218426 | 75 | 0 | 60 | 3523 | 88 | 0 | 16 | 3523 | 80 | 0 | 275 | 0 | 396267.04 | 29066863.8 | 112.48 | 8250.6
9 | DG Khan | Ghanta Ghar | Urban | 3761 | 40 | 12 | 45132 | 23 | 51 | 230173.2 | 51 | 230173.2 | 28 | 105308 | 47 | 176767 | 63 | 0 | 60 | 3761 | 88 | 0 | 16 | 3761 | 80 | 0 | 275 | 0 | 380613.2 | 24551808 | 101.2 | 6528
10 | DG Khan | Sadar Bazar-II | Urban | 4820 | 42 | 12.6 | 60732 | 27 | 56.4 | 326217.6 | 56.4 | 326217.6 | 50 | 241000 | 93 | 448260 | 69 | 0 | 60 | 4820 | 88 | 0 | 16 | 4820 | 80 | 4820 | 275 | 0 | 627949.6 | 46650852 | 130.28 | 9678.6
11 | DG Khan | Civil Line-I | Urban | 4387 | 186 | 55.8 | 244794.6 | 43 | 173.2 | 911794.08 | 173.2 | 911794.08 | 38 | 166706 | 90 | 394830 | 228 | 1 | 60 | 4387 | 88 | 4387 | 16 | 4387 | 80 | 4387 | 275 | 0 | 1323294.68 | 79131828.6 | 301.64 | 18037.8
12 | DG Khan | Civil Line-II | Urban | 1756 | 64 | 19.2 | 33715.2 | 23 | 67.8 | 142868.16 | 67.8 | 142868.16 | 368 | 646208 | 370 | 649720 | 87 | 0 | 60 | 1756 | 88 | 0 | 16 | 1756 | 80 | 1756 | 275 | 0 | 822791.36 | 47656435.2 | 468.56 | 27139.2
13 | DG Khan | Railway Road | Urban | 4293 | 62 | 18.6 | 79849.8 | 18 | 61.4 | 316308.24 | 61.4 | 316308.24 | 40 | 171720 | 82 | 352026 | 80 | 0 | 60 | 4293 | 88 | 0 | 16 | 4293 | 80 | 4293 | 275 | 0 | 567878.04 | 40339603.8 | 132.28 | 9396.6
14 | DG Khan | Industrial | Urban | 5452 | 137 | 41.1 | 224077.2 | 61 | 156.9 | 1026502.56 | 156.9 | 1026502.56 | 40 | 218080 | 167 | 910484 | 198 | 0 | 60 | 5452 | 88 | 5452 | 16 | 5452 | 80 | 5452 | 275 | 0 | 1468659.76 | 116891425.2 | 269.38 | 21440.1
15 | DG Khan | Model Town-II | Urban | 5539 | 117 | 35.1 | 194418.9 | 59 | 140.9 | 936534.12 | 140.9 | 936534.12 | 500 | 2769500 | 442 | 2448238 | 176 | 0 | 60 | 5539 | 88 | 5539 | 16 | 5539 | 80 | 5539 | 275 | 0 | 3900453.02 | 203669583.9 | 704.18 | 36770.1
16 | DG Khan | Kot Haibet | Urban | 7533 | 218 | 65.4 | 492658.2 | 157 | 309.6 | 2798660.16 | 309.6 | 2798660.16 | 59 | 444447 | 189 | 1423737 | 375 | 0 | 60 | 7533 | 88 | 7533 | 16 | 7533 | 80 | 7533 | 275 | 0 | 3735765.36 | 254821804.2 | 495.92 | 33827.4
17 | DG Khan | Shakir Town | Urban | 7043 | 131 | 39.3 | 276789.9 | 117 | 208.7 | 1763848.92 | 208.7 | 1763848.92 | 66 | 464838 | 190 | 1338170 | 248 | 0 | 60 | 7043 | 88 | 7043 | 16 | 7043 | 80 | 7043 | 275 | 0 | 2505476.82 | 186951504.9 | 355.74 | 26544.3
18 | DG Khan | Gadai-I | Urban | 3538 | 194 | 58.2 | 205911.6 | 34 | 169.8 | 720902.88 | 169.8 | 720902.88 | 35 | 123830 | 87 | 307806 | 228 | 0 | 60 | 3538 | 88 | 3538 | 16 | 3538 | 80 | 3538 | 275 | 0 | 1050644.48 | 62340267.6 | 296.96 | 17620.2
19 | DG Khan | NDVH | Urban | 387 | 45 | 13.5 | 5224.5 | 8 | 39.5 | 18343.8 | 39.5 | 18343.8 | 14 | 5418 | 16 | 6192 | 53 | 0 | 60 | 387 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 28986.3 | 1487821.5 | 74.9 | 3844.5
20 | DG Khan | Gadai-II | Urban | 2739 | 54 | 16.2 | 44371.8 | 23 | 60.8 | 199837.44 | 60.8 | 199837.44 | 666 | 1824174 | 695 | 1903605 | 77 | 0 | 60 | 2739 | 88 | 0 | 16 | 2739 | 80 | 2739 | 275 | 0 | 2068383.24 | 126339661.8 | 755.16 | 46126.2
21 | Kot Chutta | Kot Chutta | Urban | 9651 | 625 | 187.5 | 1809562.5 | 49 | 486.5 | 5634253.8 | 486.5 | 5634253.8 | 115 | 1109865 | 405 | 3908655 | 672 | 2 | 60 | 9651 | 88 | 9651 | 16 | 9651 | 80 | 9651 | 275 | 0 | 8553681.3 | 578003215.5 | 886.3 | 59890.5
22 | Rajanpur | City Rajanpur | Urban | 9538 | 345 | 103.5 | 987183 | 52 | 293.5 | 3359283.6 | 293.5 | 3359283.6 | 180 | 1716840 | 175 | 1669150 | 397 | 0 | 60 | 9538 | 88 | 9538 | 16 | 9538 | 80 | 9538 | 275 | 0 | 6063306.6 | 304667565 | 635.7 | 31942.5
23 | Rajanpur | Eid Gah Road | Urban | 4395 | 146 | 43.8 | 192501 | 40 | 142.2 | 749962.8 | 142.2 | 749962.8 | 78 | 342810 | 85 | 373575 | 186 | 0 | 60 | 4395 | 88 | 4395 | 16 | 4395 | 80 | 4395 | 275 | 0 | 1285273.8 | 67989771 | 292.44 | 15469.8
24 | Rajanpur | Railway | Urban | 5979 | 364 | 109.2 | 652906.8 | 35 | 289.8 | 2079257.04 | 289.8 | 2079257.04 | 120 | 717480 | 107 | 639753 | 399 | 0 | 60 | 5979 | 88 | 5979 | 16 | 5979 | 80 | 5979 | 275 | 0 | 3449643.84 | 165099322.8 | 576.96 | 27613.2
25 | Kot Chutta | Ashiq Abass Shaheed | Urban | 7828 | 330 | 99 | 774972 | 115 | 346 | 3250185.6 | 346 | 3250185.6 | 50 | 391400 | 101 | 790628 | 444 | 1 | 60 | 7828 | 88 | 7828 | 16 | 7828 | 80 | 7828 | 275 | 0 | 4416557.6 | 244773732 | 564.2 | 31269
26 | Kot Chutta | Jampur City-II | Urban | 6052 | 324 | 97.2 | 588254.4 | 85 | 311.8 | 2264416.32 | 311.8 | 2264416.32 | 27 | 163404 | 54 | 326808 | 409 | 0 | 60 | 6052 | 88 | 6052 | 16 | 6052 | 80 | 0 | 275 | 0 | 3016074.72 | 157238222.4 | 498.36 | 25981.2
27 | Kot Chutta | 11-KV City Jampur | Urban | 6008 | 325 | 97.5 | 585780 | 136 | 363.5 | 2620689.6 | 363.5 | 2620689.6 | 65 | 390520 | 128 | 769024 | 461 | 0 | 60 | 6008 | 88 | 6008 | 16 | 6008 | 80 | 6008 | 275 | 0 | 3596989.6 | 205140156 | 598.7 | 34144.5
28 | Rajanpur | Kot-Mithan | Urban | 6816 | 712 | 213.6 | 1455897.6 | 73 | 571.4 | 4673594.88 | 571.4 | 4673594.88 | 72 | 490752 | 106 | 722496 | 785 | 0 | 60 | 6816 | 88 | 6816 | 16 | 6816 | 80 | 6816 | 275 | 0 | 6620244.48 | 328133145.6 | 971.28 | 48141.6
29 | Rajanpur | Kot-Mithan City | Urban | 2685 | 463 | 138.9 | 372946.5 | 43 | 367.1 | 1182796.2 | 367.1 | 1182796.2 | 90 | 241650 | 76 | 204060 | 506 | 0 | 60 | 2685 | 88 | 2685 | 16 | 2685 | 80 | 0 | 275 | 0 | 1797392.7 | 84330211.5 | 669.42 | 31407.9
30 | Rajanpur | Khawaja Fareed | Urban | 9173 | 469 | 140.7 | 1290641.1 | 35 | 363.3 | 3999061.08 | 363.3 | 3999061.08 | 113 | 1036549 | 106 | 972338 | 504 | 0 | 60 | 9173 | 88 | 9173 | 16 | 9173 | 80 | 9173 | 275 | 0 | 6326251.18 | 302155868.1 | 689.66 | 32939.7
31 | Rajanpur | Fazilpur | Urban | 6986 | 703 | 210.9 | 1473347.4 | 22 | 514.1 | 4309803.12 | 514.1 | 4309803.12 | 18 | 125748 | 76 | 530936 | 725 | 0 | 60 | 6986 | 88 | 6986 | 16 | 6986 | 80 | 0 | 275 | 0 | 5908898.52 | 294864389.4 | 845.82 | 42207.9
32 | Rajanpur | Fazilpur-II | Urban | 3261 | 532 | 159.6 | 520455.6 | 18 | 390.4 | 1527713.28 | 390.4 | 1527713.28 | 546 | 1780506 | 600 | 1956600 | 550 | 0 | 60 | 3261 | 88 | 3261 | 16 | 3261 | 80 | 3261 | 275 | 0 | 3828674.88 | 210620163.6 | 1174.08 | 64587.6
33 | Taunsa | City Taunsa | Urban | 6881 | 216 | 64.8 | 445888.8 | 26 | 177.2 | 1463175.84 | 177.2 | 1463175.84 | 56 | 385336 | 125 | 860125 | 242 | 0 | 60 | 6881 | 88 | 6881 | 16 | 6881 | 80 | 6881 | 275 | 0 | 2294400.64 | 140735716.8 | 333.44 | 20452.8
34 | Taunsa | Shah Sulman | Urban | 8986 | 374 | 112.2 | 1008229.2 | 28 | 289.8 | 3124971.36 | 289.8 | 3124971.36 | 104 | 934544 | 231 | 2075766 | 402 | 0 | 60 | 8986 | 88 | 8986 | 16 | 8986 | 80 | 8986 | 275 | 0 | 5067744.56 | 315068929.2 | 563.96 | 35062.2
35 | Taunsa | Vahova | Urban | 5951 | 598 | 179.4 | 1067609.4 | 22 | 440.6 | 3146412.72 | 440.6 | 3146412.72 | 42 | 249942 | 69 | 410619 | 620 | 0 | 60 | 5951 | 88 | 5951 | 16 | 5951 | 80 | 0 | 275 | 0 | 4463964.12 | 216624731.4 | 750.12 | 36401.4
36 | Taunsa | Vahova City | Urban | 8167 | 339 | 101.7 | 830583.9 | 17 | 254.3 | 2492241.72 | 254.3 | 2492241.72 | 34 | 277678 | 93 | 759531 | 356 | 0 | 60 | 8167 | 88 | 8167 | 16 | 8167 | 80 | 8167 | 275 | 0 | 3600503.62 | 197598114.9 | 440.86 | 24194.7
|  | TOTAL |  | 204135 | 9269 | 2780.7 | 17806630.5 | 1765 | 8253.3 | 62954625 | 8253.3 | 62954625 | 3835 | 19081375 | 5872 | 31976525 | 11030 | 4 | 60 | 204135 | 88 | 182856 | 16 | 203748 | 80 | 154046 | 275 | 0 | 99842630.5 | 5749288891.5 | 489.101 | 28164.1506

## 400-220 (Urban) Vehari
Statement of 400/220 V MEPCO Consumers For 2020-21
Vehari Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | Vehari | City.No.1 | Urban | 4983 | 61 | 18.3 | 91188.9 | 10 | 52.7 | 315124.92 | 52.7 | 315124.92 | 38 | 189354 | 77 | 383691 | 71 | 0 | 60 | 4983 | 88 | 0 | 16 | 4983 | 80 | 0 | 275 | 0 | 595667.82 | 42202521.9 | 119.54 | 8469.3
2 | Vehari | Defence view | Urban | 266 | 20 | 6 | 1596 | 3 | 17 | 5426.4 | 17 | 5426.4 | 10 | 2660 | 19 | 5054 | 23 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 9682.4 | 633612 | 36.4 | 2382
3 | Vehari | Club Road | Urban | 2311 | 43 | 12.9 | 29811.9 | 10 | 40.1 | 111205.32 | 40.1 | 111205.32 | 20 | 46220 | 35 | 80885 | 53 | 0 | 60 | 2311 | 88 | 0 | 16 | 2311 | 80 | 0 | 275 | 0 | 187237.22 | 11614854.9 | 81.02 | 5025.9
4 | Vehari | C/Factory | Urban | 2340 | 113 | 33.9 | 79326 | 16 | 95.1 | 267040.8 | 95.1 | 267040.8 | 18 | 42120 | 43 | 100620 | 129 | 0 | 60 | 2340 | 88 | 2340 | 16 | 2340 | 80 | 0 | 275 | 0 | 388486.8 | 22297626 | 166.02 | 9528.9
5 | Vehari | T/Shaheed | Urban | 7080 | 133 | 39.9 | 282492 | 11 | 104.1 | 884433.6 | 104.1 | 884433.6 | 39 | 276120 | 89 | 630120 | 144 | 0 | 60 | 7080 | 88 | 7080 | 16 | 7080 | 80 | 7080 | 275 | 0 | 1443045.6 | 91720692 | 203.82 | 12954.9
6 | Vehari | City.No.2 | Urban | 4592 | 151 | 45.3 | 208017.6 | 19 | 124.7 | 687146.88 | 124.7 | 687146.88 | 27 | 123984 | 62 | 284704 | 170 | 0 | 60 | 4592 | 88 | 4592 | 16 | 4592 | 80 | 0 | 275 | 0 | 1019148.48 | 58935105.6 | 221.94 | 12834.3
7 | Vehari | City-III | Urban | 2557 | 60 | 18 | 46026 | 11 | 53 | 162625.2 | 53 | 162625.2 | 17 | 43469 | 35 | 89495 | 71 | 0 | 60 | 2557 | 88 | 0 | 16 | 2557 | 80 | 0 | 275 | 0 | 252120.2 | 15265290 | 98.6 | 5970
8 | Vehari | F/Town | Urban | 7401 | 50 | 15 | 111015 | 14 | 49 | 435178.8 | 49 | 435178.8 | 18 | 133218 | 37 | 273837 | 64 | 0 | 60 | 7401 | 88 | 0 | 16 | 7401 | 80 | 0 | 275 | 0 | 679411.8 | 42873993 | 91.8 | 5793
9 | Vehari | Madina Colony | Urban | 3845 | 36 | 10.8 | 41526 | 4 | 29.2 | 134728.8 | 29.2 | 134728.8 | 7 | 26915 | 9 | 34605 | 40 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 203169.8 | 10284606 | 52.84 | 2674.8
10 | Vehari | Balal | Urban | 5283 | 227 | 68.1 | 359772.3 | 14 | 172.9 | 1096116.84 | 172.9 | 1096116.84 | 27 | 142641 | 50 | 264150 | 241 | 0 | 60 | 5283 | 88 | 5283 | 16 | 5283 | 80 | 0 | 275 | 0 | 1598530.14 | 82695327.3 | 302.58 | 15653.1
11 | Vehari | W/Works | Urban | 1654 | 37 | 11.1 | 18359.4 | 4 | 29.9 | 59345.52 | 29.9 | 59345.52 | 19 | 31426 | 34 | 56236 | 41 | 0 | 60 | 0 | 88 | 0 | 16 | 1654 | 80 | 0 | 275 | 0 | 109130.92 | 6989969.4 | 65.98 | 4226.1
12 | Burewala | City-1 | Urban | 3931 | 74 | 22.2 | 87268.2 | 18 | 69.8 | 329260.56 | 69.8 | 329260.56 | 98 | 385238 | 147 | 577857 | 92 | 0 | 60 | 3931 | 88 | 0 | 16 | 3931 | 80 | 3931 | 275 | 0 | 801766.76 | 54688858.2 | 203.96 | 13912.2
13 | Burewala | City-6 | Urban | 2300 | 45 | 13.5 | 31050 | 2 | 33.5 | 92460 | 33.5 | 92460 | 56 | 128800 | 72 | 165600 | 47 | 0 | 60 | 0 | 88 | 0 | 16 | 2300 | 80 | 0 | 275 | 0 | 252310 | 15576750 | 109.7 | 6772.5
14 | Burewala | Ghalla Mandi | Urban | 2009 | 40 | 12 | 24108 | 3 | 31 | 74734.8 | 31 | 74734.8 | 50 | 100450 | 76 | 152684 | 43 | 0 | 60 | 0 | 88 | 0 | 16 | 2009 | 80 | 0 | 275 | 0 | 199292.8 | 13717452 | 99.2 | 6828
15 | Burewala | City No-4 | Urban | 3632 | 88 | 26.4 | 95884.8 | 15 | 76.6 | 333853.44 | 76.6 | 333853.44 | 62 | 225184 | 127 | 461264 | 103 | 0 | 60 | 3632 | 88 | 3632 | 16 | 3632 | 80 | 3632 | 275 | 0 | 654922.24 | 47994700.8 | 180.32 | 13214.4
16 | Burewala | Hameed Shaheed | Urban | 3093 | 48 | 14.4 | 44539.2 | 17 | 50.6 | 187806.96 | 50.6 | 187806.96 | 39 | 120627 | 88 | 272184 | 65 | 0 | 60 | 3093 | 88 | 0 | 16 | 3093 | 80 | 3093 | 275 | 0 | 352973.16 | 27733075.2 | 114.12 | 8966.4
17 | Burewala | Mujahid Colony | Urban | 5477 | 55 | 16.5 | 90370.5 | 14 | 52.5 | 345051 | 52.5 | 345051 | 58 | 317666 | 128 | 701056 | 69 | 0 | 60 | 5477 | 88 | 0 | 16 | 5477 | 80 | 5477 | 275 | 0 | 753087.5 | 63037531.5 | 137.5 | 11509.5
18 | Burewala | City No. 3 | Urban | 5942 | 267 | 80.1 | 475954.2 | 14 | 200.9 | 1432497.36 | 200.9 | 1432497.36 | 78 | 463476 | 160 | 950720 | 281 | 0 | 60 | 5942 | 88 | 5942 | 16 | 5942 | 80 | 5942 | 275 | 0 | 2371927.56 | 144420904.2 | 399.18 | 24305.1
19 | Burewala | City No. 5 | Urban | 4264 | 102 | 30.6 | 130478.4 | 14 | 85.4 | 436974.72 | 85.4 | 436974.72 | 75 | 319800 | 153 | 652392 | 116 | 0 | 60 | 4264 | 88 | 4264 | 16 | 4264 | 80 | 4264 | 275 | 0 | 887253.12 | 65753438.4 | 208.08 | 15420.6
20 | Burewala | City No-2 | Urban | 6900 | 112 | 33.6 | 231840 | 18 | 96.4 | 798192 | 96.4 | 798192 | 65 | 448500 | 83 | 572700 | 130 | 0 | 60 | 6900 | 88 | 6900 | 16 | 6900 | 80 | 6900 | 275 | 0 | 1478532 | 82949040 | 214.28 | 12021.6
21 | Burewala | Shabbir Shaheed | Urban | 3223 | 135 | 40.5 | 130531.5 | 15 | 109.5 | 423502.2 | 109.5 | 423502.2 | 30 | 96690 | 54 | 174042 | 150 | 0 | 60 | 3223 | 88 | 3223 | 16 | 3223 | 80 | 0 | 275 | 0 | 650723.7 | 36244246.5 | 201.9 | 11245.5
22 | Burewala | Masoom Shah | Urban | 7265 | 256 | 76.8 | 557952 | 22 | 201.2 | 1754061.6 | 201.2 | 1754061.6 | 41 | 297865 | 62 | 450430 | 278 | 0 | 60 | 7265 | 88 | 7265 | 16 | 7265 | 80 | 0 | 275 | 0 | 2609878.6 | 133943352 | 359.24 | 18436.8
23 | Burewala | Habib Colony | Urban | 7920 | 202 | 60.6 | 479952 | 35 | 176.4 | 1676505.6 | 176.4 | 1676505.6 | 62 | 491040 | 95 | 752400 | 237 | 0 | 60 | 7920 | 88 | 7920 | 16 | 7920 | 80 | 7920 | 275 | 0 | 2647497.6 | 147174192 | 334.28 | 18582.6
24 | Mailsi | City -1 | Urban | 6888 | 284 | 85.2 | 586857.6 | 27 | 225.8 | 1866372.48 | 225.8 | 1866372.48 | 75 | 516600 | 271 | 1866648 | 311 | 0 | 60 | 6888 | 88 | 6888 | 16 | 6888 | 80 | 6888 | 275 | 0 | 2969830.08 | 225741801.6 | 431.16 | 32773.2
25 | Mailsi | Fadda | Urban | 6317 | 410 | 123 | 776991 | 35 | 322 | 2440888.8 | 322 | 2440888.8 | 95 | 600115 | 204 | 1288668 | 445 | 0 | 60 | 6317 | 88 | 6317 | 16 | 6317 | 80 | 6317 | 275 | 0 | 3817994.8 | 226104381 | 604.4 | 35793
26 | Mailsi | City-2 | Urban | 6205 | 296 | 88.8 | 551004 | 23 | 230.2 | 1714069.2 | 230.2 | 1714069.2 | 133 | 825265 | 208 | 1290640 | 319 | 0 | 60 | 6205 | 88 | 6205 | 16 | 6205 | 80 | 6205 | 275 | 0 | 3090338.2 | 181935564 | 498.04 | 29320.8
27 | Mailsi | RCA | Urban | 5307 | 342 | 102.6 | 544498.2 | 25 | 264.4 | 1683804.96 | 264.4 | 1683804.96 | 107 | 567849 | 140 | 742980 | 367 | 0 | 60 | 5307 | 88 | 5307 | 16 | 5307 | 80 | 5307 | 275 | 0 | 2796152.16 | 147240592.2 | 526.88 | 27744.6
|  | TOTAL |  | 122985 | 2465 | 1106.1 | 6108410.7 | 261 | 2993.9 | 19748408.76 | 2993.9 | 19748408.76 | 712 | 6963292 | 2558 | 13275662 | 4100 | 0 | 60 | 112911 | 88 | 83158 | 16 | 118874 | 80 | 72956 | 275 | 0 | 32820111.46 | 1999769477.7 | 266.8627 | 16260.2714

## 400-220 (Urban) B-Pur
Statement of 400/220 V MEPCO Consumers For 2020-21
Bahawalpur Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | City Bahawalpur | City II | Urban | 5226 | 55 | 16.5 | 86229 | 105 | 143.5 | 899917.2 | 143.5 | 899917.2 | 10 | 52260 | 35 | 182910 | 160 | 0 | 60 | 5226 | 88 | 5226 | 16 | 0 | 80 | 0 | 275 | 0 | 1038406.2 | 65228319 | 198.7 | 12481.5
2 | City Bahawalpur | City-I | Urban | 3552 | 66 | 19.8 | 70329.6 | 78 | 124.2 | 529390.08 | 124.2 | 529390.08 | 2 | 7104 | 6 | 21312 | 144 | 0 | 60 | 3552 | 88 | 3552 | 16 | 0 | 80 | 0 | 275 | 0 | 606823.68 | 33253113.6 | 170.84 | 9361.8
3 | City Bahawalpur | Al Sadiq | Urban | 6871 | 64 | 19.2 | 131923.2 | 105 | 149.8 | 1235130.96 | 149.8 | 1235130.96 | 4 | 27484 | 17 | 116807 | 169 | 0 | 60 | 6871 | 88 | 6871 | 16 | 0 | 80 | 0 | 275 | 0 | 1394538.16 | 81512047.2 | 202.96 | 11863.2
4 | City Bahawalpur | Bwp Trade Centre | Urban | 330 | 18 | 5.4 | 1782 | 7 | 19.6 | 7761.6 | 19.6 | 7761.6 | 1 | 330 | 4 | 1320 | 25 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 9873.6 | 550242 | 29.92 | 1667.4
5 | City Bahawalpur | Al-farid | Urban | 4743 | 49 | 14.7 | 69722.1 | 9 | 43.3 | 246446.28 | 43.3 | 246446.28 | 2 | 9486 | 1 | 4743 | 58 | 0 | 60 | 4743 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 325654.38 | 15280523.1 | 68.66 | 3221.7
6 | City Bahawalpur | Baghdadul Jadeed | Urban | 8297 | 112 | 33.6 | 278779.2 | 18 | 96.4 | 959796.96 | 96.4 | 959796.96 | 32 | 265504 | 175 | 1451975 | 130 | 0 | 60 | 8297 | 88 | 8297 | 16 | 8297 | 80 | 8297 | 275 | 0 | 1504080.16 | 145542655.2 | 181.28 | 17541.6
7 | City Bahawalpur | Millat Park | Urban | 47508 | 25 | 7.5 | 356310 | 5 | 22.5 | 1282716 | 22.5 | 1282716 | 8 | 380064 | 16 | 760128 | 30 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 2019090 | 123639570 | 42.5 | 2602.5
8 | City Bahawalpur | Tibba Badar Sher | Urban | 6958 | 45 | 13.5 | 93933 | 7 | 38.5 | 321459.6 | 38.5 | 321459.6 | 23 | 160034 | 142 | 988036 | 52 | 0 | 60 | 0 | 88 | 0 | 16 | 6958 | 80 | 6958 | 275 | 0 | 575426.6 | 78851535 | 82.7 | 11332.5
9 | City Bahawalpur | Jinnah | Urban | 3520 | 52 | 15.6 | 54912 | 7 | 43.4 | 183321.6 | 43.4 | 183321.6 | 24 | 84480 | 79 | 278080 | 59 | 0 | 60 | 3520 | 88 | 0 | 16 | 3520 | 80 | 0 | 275 | 0 | 322713.6 | 27848832 | 91.68 | 7911.6
10 | City Bahawalpur | Satellite Town | Urban | 2714 | 67 | 20.1 | 54551.4 | 78 | 124.9 | 406774.32 | 124.9 | 406774.32 | 104 | 282256 | 84 | 227976 | 145 | 0 | 60 | 2714 | 88 | 2714 | 16 | 2714 | 80 | 2714 | 275 | 0 | 743581.72 | 38248673.4 | 273.98 | 14093.1
11 | City Bahawalpur | Islami Colony | Urban | 8289 | 71 | 21.3 | 176555.7 | 63 | 112.7 | 1121004.36 | 112.7 | 1121004.36 | 7 | 58023 | 20 | 165780 | 134 | 0 | 60 | 8289 | 88 | 8289 | 16 | 0 | 80 | 0 | 275 | 0 | 1355583.06 | 77736728.7 | 163.54 | 9378.3
12 | City Bahawalpur | Darbar Mehal | Urban | 4849 | 100 | 30 | 145470 | 3 | 73 | 424772.4 | 73 | 424772.4 | 11 | 53339 | 62 | 300638 | 103 | 0 | 60 | 4849 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 623581.4 | 43961034 | 128.6 | 9066
13 | City Bahawalpur | Bahawal | Urban | 4773 | 103 | 30.9 | 147485.7 | 13 | 85.1 | 487418.76 | 85.1 | 487418.76 | 0 | 0 | 0 | 0 | 116 | 0 | 60 | 4773 | 88 | 4773 | 16 | 0 | 80 | 0 | 275 | 0 | 634904.46 | 29687582.7 | 133.02 | 6219.9
14 | City Bahawalpur | Gulzar Mehal | Urban | 7298 | 171 | 51.3 | 374387.4 | 5 | 124.7 | 1092072.72 | 124.7 | 1092072.72 | 2 | 14596 | 1 | 7298 | 176 | 0 | 60 | 7298 | 88 | 7298 | 16 | 0 | 80 | 0 | 275 | 0 | 1481056.12 | 67085405.4 | 202.94 | 9192.3
15 | City Bahawalpur | City 1 Yazman | Urban | 4849 | 104 | 31.2 | 151288.8 | 51 | 123.8 | 720367.44 | 123.8 | 720367.44 | 4 | 19396 | 22 | 106678 | 155 | 0 | 60 | 4849 | 88 | 4849 | 16 | 0 | 80 | 0 | 275 | 0 | 891052.24 | 50076592.8 | 183.76 | 10327.2
16 | City Bahawalpur | City 2 | Urban | 5647 | 111 | 33.3 | 188045.1 | 30 | 107.7 | 729818.28 | 107.7 | 729818.28 | 3 | 16941 | 18 | 101646 | 141 | 0 | 60 | 5647 | 88 | 5647 | 16 | 0 | 80 | 0 | 275 | 0 | 934804.38 | 50451992.1 | 165.54 | 8934.3
17 | City Bahawalpur | College Road | Urban | 5467 | 125 | 37.5 | 205012.5 | 70 | 157.5 | 1033263 | 157.5 | 1033263 | 2 | 10934 | 9 | 49203 | 195 | 0 | 60 | 5467 | 88 | 5467 | 16 | 0 | 80 | 0 | 275 | 0 | 1249209.5 | 65562997.5 | 228.5 | 11992.5
18 | City Bahawalpur | Rehman City | Urban | 6 | 3 | 0.9 | 5.4 | 3 | 5.1 | 36.72 | 5.1 | 36.72 | 1 | 6 | 6 | 36 | 6 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 48.12 | 4379.4 | 8.02 | 729.9
19 | Lodhran | Shah Hussain | Urban | 3112 | 390 | 117 | 364104 | 87 | 360 | 1344384 | 360 | 1344384 | 10 | 31120 | 42 | 130704 | 476 | 1 | 60 | 3112 | 88 | 3112 | 16 | 0 | 80 | 0 | 275 | 0 | 1739608 | 89597592 | 559 | 28791
20 | Lodhran | City-2 | Urban | 4850 | 111 | 33.3 | 161505 | 43 | 120.7 | 702474 | 120.7 | 702474 | 7 | 33950 | 23 | 111550 | 153 | 1 | 60 | 4850 | 88 | 4850 | 16 | 0 | 80 | 0 | 275 | 0 | 897929 | 49325955 | 185.14 | 10170.3
21 | Lodhran | City-3 | Urban | 949 | 75 | 22.5 | 21352.5 | 46 | 98.5 | 112171.8 | 98.5 | 112171.8 | 9 | 8541 | 34 | 32266 | 120 | 1 | 60 | 949 | 88 | 949 | 16 | 0 | 80 | 0 | 275 | 0 | 142065.3 | 8730325.5 | 149.7 | 9199.5
22 | Lodhran | City Jallah | Urban | 3922 | 170 | 51 | 200022 | 51 | 170 | 800088 | 170 | 800088 | 5 | 19610 | 11 | 43142 | 221 | 0 | 60 | 3922 | 88 | 3922 | 16 | 0 | 80 | 0 | 275 | 0 | 1019720 | 51193866 | 260 | 13053
23 | Lodhran | Model View | Urban | 4 | 3 | 0.9 | 3.6 | 2 | 4.1 | 19.68 | 4.1 | 19.68 | 2 | 8 | 5 | 20 | 4 | 1 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 31.28 | 2391.6 | 7.82 | 597.9
24 | Lodhran | City II | Urban | 9530 | 237 | 71.1 | 677583 | 83 | 248.9 | 2846420.4 | 248.9 | 2846420.4 | 16 | 152480 | 50 | 476500 | 319 | 1 | 60 | 9530 | 88 | 9530 | 16 | 0 | 80 | 0 | 275 | 0 | 3676483.4 | 201407973 | 385.78 | 21134.1
25 | Lodhran | City Lodhran | Urban | 8383 | 128 | 38.4 | 321907.2 | 84 | 173.6 | 1746346.56 | 173.6 | 1746346.56 | 190 | 1592770 | 101 | 846683 | 211 | 1 | 60 | 8383 | 88 | 8383 | 16 | 8383 | 80 | 8383 | 275 | 0 | 3661023.76 | 156547495.2 | 436.72 | 18674.4
26 | Lodhran | Colony | Urban | 10304 | 160 | 48 | 494592 | 55 | 167 | 2064921.6 | 167 | 2064921.6 | 6 | 61824 | 37 | 381248 | 214 | 1 | 60 | 10304 | 88 | 10304 | 16 | 0 | 80 | 0 | 275 | 0 | 2621337.6 | 148253952 | 254.4 | 14388
27 | Lodhran | Khawaja Chowk | Rural | 10 | 112 | 33.6 | 336 | 29 | 107.4 | 1288.8 | 107.4 | 1288.8 | 4 | 40 | 13 | 130 | 140 | 1 | 60 | 10 | 88 | 10 | 16 | 0 | 80 | 0 | 275 | 0 | 1664.8 | 86136 | 166.48 | 8613.6
28 | A.P East | Abbasia | Urban | 9088 | 36 | 10.8 | 98150.4 | 65 | 90.2 | 983685.12 | 90.2 | 983685.12 | 12 | 109056 | 35 | 318080 | 101 | 0 | 60 | 9088 | 88 | 9088 | 16 | 0 | 80 | 0 | 275 | 0 | 1190891.52 | 78400358.4 | 131.04 | 8626.8
29 | A.P East | City A.p.east | Urban | 6092 | 15 | 4.5 | 27414 | 20 | 30.5 | 222967.2 | 30.5 | 222967.2 | 13 | 79196 | 40 | 243680 | 35 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 329577.2 | 28081074 | 54.1 | 4609.5
30 | A.P East | City-2 | Urban | 7325 | 48 | 14.4 | 105480 | 27 | 60.6 | 532674 | 60.6 | 532674 | 15 | 109875 | 40 | 293000 | 75 | 0 | 60 | 7325 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 748029 | 49856880 | 102.12 | 6806.4
31 | A.P East | Uch Road | Urban | 4688 | 90 | 27 | 126576 | 29 | 92 | 517555.2 | 92 | 517555.2 | 15 | 70320 | 41 | 192208 | 119 | 0 | 60 | 4688 | 88 | 4688 | 16 | 0 | 80 | 0 | 275 | 0 | 714451.2 | 42965520 | 152.4 | 9165
32 | A.P East | Dera Nawab | Urban | 8610 | 74 | 22.2 | 191142 | 65 | 116.8 | 1206777.6 | 116.8 | 1206777.6 | 15 | 129150 | 35 | 301350 | 139 | 0 | 60 | 8610 | 88 | 8610 | 16 | 0 | 80 | 0 | 275 | 0 | 1527069.6 | 91061082 | 177.36 | 10576.2
33 | A.P East | Channi Goth | Urban | 5438 | 170 | 51 | 277338 | 51 | 170 | 1109352 | 170 | 1109352 | 17 | 92446 | 51 | 277338 | 221 | 0 | 60 | 5438 | 88 | 5438 | 16 | 5438 | 80 | 0 | 275 | 0 | 1479136 | 84033414 | 272 | 15453
34 | A.P East | City | Urban | 7583 | 120 | 36 | 272988 | 8 | 92 | 837163.2 | 92 | 837163.2 | 11 | 83413 | 33 | 250239 | 128 | 0 | 60 | 7583 | 88 | 7583 | 16 | 0 | 80 | 0 | 275 | 0 | 1193564.2 | 66063096 | 157.4 | 8712
35 | A.P East | City Mubarak Pur | Urban | 4385 | 140 | 42 | 184170 | 18 | 116 | 610392 | 116 | 610392 | 11 | 48235 | 31 | 135935 | 158 | 0 | 60 | 4385 | 88 | 4385 | 16 | 0 | 80 | 0 | 275 | 0 | 842797 | 45332130 | 192.2 | 10338
36 | A.P East | Uch City | Urban | 8183 | 70 | 21 | 171843 | 4 | 53 | 520438.8 | 53 | 520438.8 | 15 | 122745 | 41 | 335503 | 74 | 0 | 60 | 8183 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 815026.8 | 51872037 | 99.6 | 6339
37 | A.P East | Uch Mughlan | Urban | 3385 | 15 | 4.5 | 15232.5 | 4 | 14.5 | 58899 | 14.5 | 58899 | 15 | 50775 | 41 | 138785 | 19 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 124906.5 | 11906737.5 | 36.9 | 3517.5
38 | A.P East | MES Army | Urban | 25 | 28 | 8.4 | 210 | 6 | 25.6 | 768 | 25.6 | 768 | 15 | 375 | 15 | 375 | 33 | 1 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 1353 | 69210 | 54.12 | 2768.4
39 | Model Town | City_khanqah | Urban | 4704 | 164 | 49.2 | 231436.8 | 37 | 151.8 | 856880.64 | 151.8 | 856880.64 | 15 | 70560 | 6 | 28224 | 17 | 0 | 60 | 4704 | 88 | 4704 | 16 | 0 | 80 | 0 | 275 | 0 | 1158877.44 | 53800588.8 | 246.36 | 11437.2
40 | Model Town | Model Avenue | Urban | 87 | 41 | 12.3 | 1070.1 | 7 | 35.7 | 3727.08 | 35.7 | 3727.08 | 15 | 1305 | 141 | 12267 | 221 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 87 | 275 | 0 | 6102.18 | 962855.1 | 70.14 | 11067.3
41 | Model Town | Seerani | Urban | 7608 | 190 | 57 | 433656 | 30 | 163 | 1488124.8 | 163 | 1488124.8 | 15 | 114120 | 7 | 53256 | 26 | 0 | 60 | 7608 | 88 | 7608 | 16 | 0 | 80 | 0 | 275 | 0 | 2035900.8 | 93783816 | 267.6 | 12327
42 | Model Town | Canal Garden | Urban | 59 | 21 | 6.3 | 371.7 | 5 | 19.7 | 1394.76 | 19.7 | 1394.76 | 268 | 15812 | 268 | 15812 | 26 | 0 | 60 | 0 | 88 | 0 | 16 | 59 | 80 | 59 | 275 | 0 | 17578.46 | 1033520.7 | 297.94 | 17517.3
43 | Model Town | Dera Izzat | Urban | 4017 | 102 | 30.6 | 122920.2 | 47 | 118.4 | 570735.36 | 118.4 | 570735.36 | 4 | 16068 | 7 | 28119 | 149 | 0 | 60 | 4017 | 88 | 4017 | 16 | 0 | 80 | 0 | 275 | 0 | 709723.56 | 36300022.2 | 176.68 | 9036.6
44 | Model Town | Hashmi Garden | Urban | 3868 | 115 | 34.5 | 133446 | 4 | 84.5 | 392215.2 | 84.5 | 392215.2 | 1 | 3868 | 1 | 3868 | 119 | 0 | 60 | 3868 | 88 | 3868 | 16 | 0 | 80 | 0 | 275 | 0 | 529529.2 | 24165330 | 136.9 | 6247.5
45 | Model Town | Hoot_wala | Urban | 7265 | 327 | 98.1 | 712696.5 | 22 | 250.9 | 2187346.2 | 250.9 | 2187346.2 | 136 | 988040 | 135 | 980775 | 349 | 0 | 60 | 7265 | 88 | 7265 | 16 | 7265 | 80 | 7265 | 275 | 0 | 3888082.7 | 192225361.5 | 535.18 | 26459.1
46 | Model Town | Model Town A | Urban | 3297 | 64 | 19.2 | 63302.4 | 88 | 132.8 | 525409.92 | 132.8 | 525409.92 | 3 | 9891 | 14 | 46158 | 152 | 0 | 60 | 3297 | 88 | 3297 | 16 | 0 | 80 | 0 | 275 | 0 | 598603.32 | 34483982.4 | 181.56 | 10459.2
47 | Model Town | NlC | Urban | 1971 | 46 | 13.8 | 27199.8 | 3 | 35.2 | 83255.04 | 35.2 | 83255.04 | 1 | 1971 | 1 | 1971 | 49 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 112425.84 | 5195161.8 | 57.04 | 2635.8
48 | Model Town | Noor Mahal | Urban | 5019 | 71 | 21.3 | 106904.7 | 71 | 120.7 | 726951.96 | 120.7 | 726951.96 | 7 | 35133 | 31 | 155589 | 142 | 0 | 60 | 5019 | 88 | 5019 | 16 | 0 | 80 | 0 | 275 | 0 | 868989.66 | 53273171.7 | 173.14 | 10614.3
49 | Model Town | P.g.s Housing Scheme | Urban | 138 | 58 | 17.4 | 2401.2 | 25 | 65.6 | 10863.36 | 65.6 | 10863.36 | 191 | 26358 | 205 | 28290 | 83 | 0 | 60 | 138 | 88 | 0 | 16 | 138 | 80 | 138 | 275 | 0 | 39622.56 | 2356405.2 | 287.12 | 17075.4
50 | Model Town | University Campus | Urban | 6559 | 85 | 25.5 | 167254.5 | 86 | 145.5 | 1145201.4 | 145.5 | 1145201.4 | 8 | 52472 | 36 | 236124 | 171 | 0 | 60 | 6559 | 88 | 6559 | 16 | 0 | 80 | 0 | 275 | 0 | 1364927.9 | 83381287.5 | 208.1 | 12712.5
51 | Model Town | Al-rehman | Urban | 5395 | 100 | 30 | 161850 | 98 | 168 | 1087632 | 168 | 1087632 | 4 | 21580 | 18 | 97110 | 198 | 0 | 60 | 5395 | 88 | 5395 | 16 | 0 | 80 | 0 | 275 | 0 | 1271062 | 71570070 | 235.6 | 13266
52 | Model Town | Badaruddin Shaheed | Urban | 6485 | 99 | 29.7 | 192604.5 | 100 | 169.3 | 1317492.6 | 169.3 | 1317492.6 | 1 | 6485 | 4 | 25940 | 199 | 0 | 60 | 6485 | 88 | 6485 | 16 | 0 | 80 | 0 | 275 | 0 | 1516582.1 | 81183769.5 | 233.86 | 12518.7
53 | Model Town | Bindrah Pully | Urban | 4299 | 100 | 30 | 128970 | 83 | 153 | 789296.4 | 153 | 789296.4 | 1 | 4299 | 4 | 17196 | 183 | 0 | 60 | 4299 | 88 | 4299 | 16 | 0 | 80 | 0 | 275 | 0 | 922565.4 | 48776454 | 214.6 | 11346
54 | Model Town | College Road-i | Urban | 8359 | 28 | 8.4 | 70215.6 | 25 | 44.6 | 447373.68 | 44.6 | 447373.68 | 1 | 8359 | 3 | 25077 | 53 | 0 | 60 | 8359 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 525948.28 | 28557687.6 | 62.92 | 3416.4
55 | Model Town | College Road-ii | Urban | 5800 | 24 | 7.2 | 41760 | 32 | 48.8 | 339648 | 48.8 | 339648 | 1 | 5800 | 2 | 11600 | 56 | 0 | 60 | 5800 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 387208 | 21200160 | 66.76 | 3655.2
56 | Model Town | Industrial Estate | Urban | 3996 | 90 | 27 | 107892 | 63 | 126 | 604195.2 | 126 | 604195.2 | 8 | 31968 | 32 | 127872 | 153 | 0 | 60 | 3996 | 88 | 3996 | 16 | 0 | 80 | 0 | 275 | 0 | 744055.2 | 44247708 | 186.2 | 11073
57 | Model Town | Shadman City | Urban | 398 | 12 | 3.6 | 1432.8 | 19 | 27.4 | 13086.24 | 27.4 | 13086.24 | 1 | 398 | 1 | 398 | 31 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 14917.04 | 813352.8 | 37.48 | 2043.6
58 | Model Town | Model Town B | Urban | 5269 | 49 | 14.7 | 77454.3 | 87 | 121.3 | 766955.64 | 121.3 | 766955.64 | 7 | 36883 | 1.35 | 7113.15 | 136 | 0 | 60 | 5269 | 88 | 5269 | 16 | 0 | 80 | 0 | 275 | 0 | 881292.94 | 46676490.3 | 167.26 | 8858.7
59 | Model Town | Model Town C | Urban | 3591 | 30 | 9 | 32319 | 45 | 66 | 284407.2 | 66 | 284407.2 | 7 | 25137 | 32.4 | 116348.4 | 75 | 0 | 60 | 3591 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 341863.2 | 24142293 | 95.2 | 6723
60 | Model Town | Paragon City | Urban | 162 | 28 | 8.4 | 1360.8 | 11 | 30.6 | 5948.64 | 30.6 | 5948.64 | 2 | 324 | 9.55 | 1547.1 | 39 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 7633.44 | 453826.8 | 47.12 | 2801.4
61 | Model Town | Satluj | Urban | 4332 | 339 | 101.7 | 440564.4 | 148 | 385.3 | 2002943.52 | 385.3 | 2002943.52 | 1 | 4332 | 4.05 | 17544.6 | 487 | 0 | 60 | 4332 | 88 | 4332 | 16 | 0 | 80 | 0 | 275 | 0 | 2447839.92 | 122550980.4 | 565.06 | 28289.7
62 | Model Town | Shahdara | Urban | 5306 | 42 | 12.6 | 66855.6 | 52 | 81.4 | 518290.08 | 81.4 | 518290.08 | 11 | 58366 | 36.4 | 193138.4 | 94 | 0 | 60 | 5306 | 88 | 5306 | 16 | 0 | 80 | 0 | 275 | 0 | 643511.68 | 42886275.6 | 121.28 | 8082.6
63 | Hasil Pur | City Hasilpur | Urban | 7923 | 92 | 27.6 | 218674.8 | 8 | 72.4 | 688350.24 | 72.4 | 688350.24 | 139 | 1101297 | 120 | 950760 | 100 | 0 | 60 | 7923 | 88 | 0 | 16 | 7923 | 80 | 7923 | 275 | 0 | 2008322.04 | 99002638.8 | 253.48 | 12495.6
64 | Hasil Pur | City -II | Urban | 4587 | 87 | 26.1 | 119720.7 | 9 | 69.9 | 384757.56 | 69.9 | 384757.56 | 117 | 536679 | 91 | 417417 | 96 | 0 | 60 | 4587 | 88 | 0 | 16 | 4587 | 80 | 4587 | 275 | 0 | 1041157.26 | 48489635.7 | 226.98 | 10571.1
65 | Hasil Pur | Hospital | Urban | 4717 | 75 | 22.5 | 106132.5 | 12 | 64.5 | 365095.8 | 64.5 | 365095.8 | 141 | 665097 | 96 | 452832 | 87 | 0 | 60 | 4717 | 88 | 0 | 16 | 4717 | 80 | 4717 | 275 | 0 | 1136325.3 | 49394065.5 | 240.9 | 10471.5
66 | Hasil Pur | City Kpt | Urban | 3695 | 85 | 25.5 | 94222.5 | 14 | 73.5 | 325899 | 73.5 | 325899 | 39 | 144105 | 71 | 262345 | 99 | 0 | 60 | 3695 | 88 | 3695 | 16 | 3695 | 80 | 0 | 275 | 0 | 564226.5 | 35577307.5 | 152.7 | 9628.5
67 | Hasil Pur | Railway Road | Urban | 5456 | 125 | 37.5 | 204600 | 13 | 100.5 | 657993.6 | 100.5 | 657993.6 | 41 | 223696 | 63 | 343728 | 138 | 0 | 60 | 5456 | 88 | 5456 | 16 | 5456 | 80 | 0 | 275 | 0 | 1086289.6 | 60717096 | 199.1 | 11128.5
68 | Hasil Pur | Islam Pura | Urban | 2886 | 57 | 17.1 | 49350.6 | 2 | 41.9 | 145108.08 | 41.9 | 145108.08 | 25 | 72150 | 35 | 101010 | 59 | 0 | 60 | 2886 | 88 | 0 | 16 | 2886 | 80 | 0 | 275 | 0 | 266608.68 | 14915136.6 | 92.38 | 5168.1
69 | Hasil Pur | Old Hasil Pur | Urban | 6316 | 276 | 82.8 | 522964.8 | 18 | 211.2 | 1600727.04 | 211.2 | 1600727.04 | 97 | 612652 | 123 | 776868 | 294 | 0 | 60 | 6316 | 88 | 6316 | 16 | 6316 | 80 | 6316 | 275 | 0 | 2736343.84 | 144224596.8 | 433.24 | 22834.8
70 | Hasil Pur | stown_hasilp | Urban | 3480 | 43 | 12.9 | 44892 | 8 | 38.1 | 159105.6 | 38.1 | 159105.6 | 69 | 240120 | 88 | 306240 | 51 | 0 | 60 | 0 | 88 | 0 | 16 | 3480 | 80 | 3480 | 275 | 0 | 444117.6 | 28055412 | 127.62 | 8061.9
71 | Hasil Pur | Vehari_road | Urban | 5002 | 66 | 19.8 | 99039.6 | 9 | 55.2 | 331332.48 | 55.2 | 331332.48 | 75 | 375150 | 64 | 320128 | 75 | 0 | 60 | 5002 | 88 | 0 | 16 | 5002 | 80 | 0 | 275 | 0 | 805522.08 | 39384747.6 | 161.04 | 7873.8
72 | Kahror Pacca | City Duniya Pur | Urban | 5212 | 109 | 32.7 | 170432.4 | 12 | 88.3 | 552263.52 | 88.3 | 552263.52 | 73 | 380476 | 172 | 896464 | 121 | 0 | 60 | 5212 | 88 | 5212 | 16 | 5212 | 80 | 5212 | 275 | 0 | 1103171.92 | 87434948.4 | 211.66 | 16775.7
73 | Kahror Pacca | Noor Pir | Urban | 3914 | 144 | 43.2 | 169084.8 | 7 | 107.8 | 506315.04 | 107.8 | 506315.04 | 79 | 309206 | 177 | 692778 | 151 | 0 | 60 | 3914 | 88 | 3914 | 16 | 3914 | 80 | 3914 | 275 | 0 | 984605.84 | 72452836.8 | 251.56 | 18511.2
74 | Kahror Pacca | Model Town | Urban | 2924 | 147 | 44.1 | 128948.4 | 14 | 116.9 | 410178.72 | 116.9 | 410178.72 | 69 | 201756 | 164 | 479536 | 161 | 0 | 60 | 2924 | 88 | 2924 | 16 | 2924 | 80 | 2924 | 275 | 0 | 740883.12 | 53769728.4 | 253.38 | 18389.1
75 | Kahror Pacca | City Kehror Pacca | Urban | 3861 | 101 | 30.3 | 116988.3 | 6 | 76.7 | 355366.44 | 76.7 | 355366.44 | 28 | 108108 | 54 | 208494 | 107 | 0 | 60 | 3861 | 88 | 3861 | 16 | 3861 | 80 | 0 | 275 | 0 | 580462.74 | 34182591.3 | 150.34 | 8853.3
76 | Kahror Pacca | City-2 | Urban | 6037 | 99 | 29.7 | 179298.9 | 5 | 74.3 | 538258.92 | 74.3 | 538258.92 | 244 | 1473028 | 83 | 501071 | 104 | 0 | 60 | 6037 | 88 | 6037 | 16 | 6037 | 80 | 6037 | 275 | 0 | 2190585.82 | 62897691.9 | 362.86 | 10418.7
77 | Kahror Pacca | Main Bazar | Urban | 4804 | 81 | 24.3 | 116737.2 | 8 | 64.7 | 372982.56 | 64.7 | 372982.56 | 38 | 182552 | 148 | 710992 | 89 | 0 | 60 | 4804 | 88 | 0 | 16 | 4804 | 80 | 4804 | 275 | 0 | 672271.76 | 65388685.2 | 139.94 | 13611.3
78 | Kahror Pacca | Tibba Sadat | Urban | 3631 | 55 | 16.5 | 59911.5 | 3 | 41.5 | 180823.8 | 41.5 | 180823.8 | 251 | 911381 | 101 | 366731 | 58 | 0 | 60 | 3631 | 88 | 0 | 16 | 3631 | 80 | 3631 | 275 | 0 | 1152116.3 | 33033022.5 | 317.3 | 9097.5
|  | TOTAL |  | 409192 | 7400 | 2220 | 12025609.2 | 2770 | 7950 | 51644188.56 | 7950 | 51644188.56 | 2877 | 13315148 | 4065.75 | 19292033.65 | 9956 | 9 | 60 | 338727 | 88 | 258669 | 16 | 117217 | 80 | 87446 | 275 | 0 | 76984945.76 | 4292250160.2 | 188.1389 | 10489.575

## 400-220 (Urban) Sahiwal
Statement of 400/220 V MEPCO Consumers For 2020-21
Sahiwal Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | Sahiwal-1 | College Road | Urban | 5039 | 137 | 41.1 | 207102.9 | 10 | 105.9 | 640356.12 | 105.9 | 640356.12 | 147 | 740733 | 178.38 | 898856.82 | 147 | 0 | 60 | 5039 | 88 | 5039 | 16 | 5039 | 80 | 5039 | 275 | 0 | 1588192.02 | 92974085.1 | 315.18 | 18450.9
2 | Sahiwal-1 | TV Corporation | Urban | 3104 | 50 | 15 | 46560 | 9 | 44 | 163891.2 | 44 | 163891.2 | 52 | 161408 | 59.32 | 184129.28 | 58 | 1 | 60 | 3104 | 88 | 0 | 16 | 3104 | 80 | 0 | 275 | 0 | 371859.2 | 21020908.8 | 119.8 | 6772.2
3 | Sahiwal-1 | Civil Hospital | Urban | 4651 | 70 | 21 | 97671 | 9 | 58 | 323709.6 | 58 | 323709.6 | 129 | 599979 | 144.27 | 670999.77 | 79 | 0 | 60 | 4651 | 88 | 0 | 16 | 4651 | 80 | 4651 | 275 | 0 | 1021359.6 | 59975575.2 | 219.6 | 12895.2
4 | Sahiwal-1 | Shadman | Urban | 6690 | 147 | 44.1 | 295029 | 12 | 114.9 | 922417.2 | 114.9 | 922417.2 | 142 | 949980 | 181.15 | 1211893.5 | 159 | 0 | 60 | 6690 | 88 | 6690 | 16 | 6690 | 80 | 6690 | 275 | 0 | 2167426.2 | 128943729 | 323.98 | 19274.1
5 | Sahiwal-1 | Chak 85/6-R | Urban | 5219 | 151 | 45.3 | 236420.7 | 21 | 126.7 | 793496.76 | 126.7 | 793496.76 | 119 | 621061 | 111.5 | 581918.5 | 172 | 0 | 60 | 5219 | 88 | 5219 | 16 | 5219 | 80 | 5219 | 275 | 0 | 1650978.46 | 83234177.7 | 316.34 | 15948.3
6 | Sahiwal-1 | Ratti Tibbi | Urban | 4520 | 305 | 91.5 | 413580 | 30 | 243.5 | 1320744 | 243.5 | 1320744 | 132 | 596640 | 104.41 | 471933.2 | 335 | 0 | 60 | 4520 | 88 | 4520 | 16 | 4520 | 80 | 4520 | 275 | 0 | 2330964 | 108801372 | 515.7 | 24071.1
7 | Sahiwal-1 | Ashiyana Scheme | Urban | 127 | 18 | 5.4 | 685.8 | 0 | 12.6 | 1920.24 | 12.6 | 1920.24 | 7 | 889 | 13.4 | 1701.8 | 18 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 3495.04 | 219379.8 | 27.52 | 1727.4
8 | Sahiwal-1 | Rafi Garden | Urban | 429 | 25 | 7.5 | 3217.5 | 3 | 20.5 | 10553.4 | 20.5 | 10553.4 | 5 | 2145 | 2.12 | 909.48 | 28 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 15915.9 | 697425.3 | 37.1 | 1625.7
9 | Sahiwal-1 | Tariq Bin Ziad | Urban | 3721 | 77 | 23.1 | 85955.1 | 11 | 64.9 | 289791.48 | 64.9 | 289791.48 | 55 | 204655 | 65.39 | 243316.19 | 88 | 0 | 60 | 3721 | 88 | 0 | 16 | 3721 | 80 | 0 | 275 | 0 | 580401.58 | 32244325.5 | 155.98 | 8665.5
10 | Sahiwal-1 | Ghalla Mandi | Urban | 5508 | 65 | 19.5 | 107406 | 55 | 100.5 | 664264.8 | 100.5 | 664264.8 | 9 | 49572 | 5 | 27540 | 120 | 0 | 60 | 5508 | 88 | 5508 | 16 | 0 | 80 | 0 | 275 | 0 | 821242.8 | 41830506 | 149.1 | 7594.5
11 | Sahiwal-1 | Shadab Town | Urban | 6593 | 167 | 50.1 | 330309.3 | 74 | 190.9 | 1510324.44 | 190.9 | 1510324.44 | 8 | 52744 | 38.5 | 253830.5 | 241 | 0 | 60 | 6593 | 88 | 6593 | 16 | 0 | 80 | 0 | 275 | 0 | 1893377.74 | 106840224.3 | 287.18 | 16205.1
12 | Sahiwal-1 | Pakpattan Road | Urban | 4073 | 55 | 16.5 | 67204.5 | 15 | 53.5 | 261486.6 | 53.5 | 261486.6 | 7 | 28511 | 17 | 69241 | 70 | 0 | 60 | 4073 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 357202.1 | 20045269.5 | 87.7 | 4921.5
13 | Sahiwal-1 | 81/5-R | Urban | 3924 | 110 | 33 | 129492 | 11 | 88 | 414374.4 | 88 | 414374.4 | 60 | 235440 | 69.59 | 273071.16 | 121 | 0 | 60 | 3924 | 88 | 3924 | 16 | 3924 | 80 | 0 | 275 | 0 | 779306.4 | 41635209.6 | 198.6 | 10610.4
14 | Sahiwal-1 | Lahore Road | Urban | 5350 | 85 | 25.5 | 136425 | 10 | 69.5 | 446190 | 69.5 | 446190 | 23 | 123050 | 12 | 64200 | 95 | 0 | 60 | 5350 | 88 | 0 | 16 | 5350 | 80 | 0 | 275 | 0 | 705665 | 31032675 | 131.9 | 5800.5
15 | Sahiwal-1 | Allama Iqbal | Urban | 4054 | 35 | 10.5 | 42567 | 9 | 33.5 | 162970.8 | 33.5 | 162970.8 | 21 | 85134 | 18 | 72972 | 44 | 0 | 60 | 0 | 88 | 0 | 16 | 4054 | 80 | 0 | 275 | 0 | 290671.8 | 14284269 | 71.7 | 3523.5
16 | Sahiwal-1 | Grid Colony | Urban | 103 | 12 | 3.6 | 370.8 | 14 | 22.4 | 2768.64 | 22.4 | 2768.64 | 19 | 1957 | 19 | 1957 | 26 | 0 | 60 | 0 | 88 | 0 | 16 | 103 | 80 | 0 | 275 | 0 | 5096.44 | 284650.8 | 49.48 | 2763.6
17 | Sahiwal-1 | Royal Palm | Urban | 287 | 14 | 4.2 | 1205.4 | 21 | 30.8 | 10607.52 | 30.8 | 10607.52 | 5 | 1435 | 30.4 | 8724.8 | 35 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 13247.92 | 1163555.4 | 46.16 | 4054.2
18 | Sahiwal-1 | Bilal Colony | Urban | 4864 | 113 | 33.9 | 164889.6 | 8 | 87.1 | 508385.28 | 87.1 | 508385.28 | 83 | 403712 | 112.26 | 546032.64 | 121 | 0 | 60 | 4864 | 88 | 4864 | 16 | 4864 | 80 | 4864 | 275 | 0 | 1076986.88 | 63759744 | 221.42 | 13108.5
19 | Sahiwal-1 | Scheme No.3 | Urban | 3581 | 90 | 27 | 96687 | 4 | 67 | 287912.4 | 67 | 287912.4 | 45 | 161145 | 59.33 | 212460.73 | 94 | 0 | 60 | 3581 | 88 | 0 | 16 | 3581 | 80 | 0 | 275 | 0 | 545744.4 | 30312448.8 | 152.4 | 8464.8
20 | Sahiwal-1 | Civil Line | Urban | 2936 | 111 | 33.3 | 97768.8 | 82 | 159.7 | 562655.04 | 159.7 | 562655.04 | 21 | 61656 | 110.55 | 324574.8 | 192 | 1 | 60 | 2936 | 88 | 2936 | 16 | 2936 | 80 | 2936 | 275 | 0 | 722079.84 | 53527096.8 | 245.94 | 18231.3
21 | Sahiwal-1 | Ali Garh | Urban | 5119 | 70 | 21 | 107499 | 5 | 54 | 331711.2 | 54 | 331711.2 | 37 | 189403 | 103.15 | 528024.85 | 75 | 0 | 60 | 5119 | 88 | 0 | 16 | 5119 | 80 | 5119 | 275 | 0 | 628613.2 | 51906660 | 122.8 | 10140
22 | Sahiwal-1 | Fareed Town | Urban | 3234 | 85 | 25.5 | 82467 | 5 | 64.5 | 250311.6 | 64.5 | 250311.6 | 56 | 181104 | 72.25 | 233656.5 | 90 | 0 | 60 | 3234 | 88 | 0 | 16 | 3234 | 80 | 0 | 275 | 0 | 513882.6 | 29285487 | 158.9 | 9055.5
23 | Sahiwal-2nd | Ansar | Urban | 3772 | 37 | 11.1 | 41869.2 | 4 | 29.9 | 135339.36 | 29.9 | 135339.36 | 41 | 154652 | 50.47 | 190372.84 | 41 | 0 | 60 | 0 | 88 | 0 | 16 | 3772 | 80 | 0 | 275 | 0 | 331860.56 | 19668339.6 | 87.98 | 5214.3
24 | Sahiwal-2nd | Baba Frid | Urban | 5770 | 24 | 7.2 | 41544 | 6 | 22.8 | 157867.2 | 22.8 | 157867.2 | 32 | 184640 | 45 | 259650 | 30 | 0 | 60 | 0 | 88 | 0 | 16 | 5770 | 80 | 0 | 275 | 0 | 384051.2 | 25175664 | 66.56 | 4363.2
25 | Sahiwal-2nd | Multan Road | Urban | 2909 | 93 | 27.9 | 81161.1 | 116 | 181.1 | 632183.88 | 181.1 | 632183.88 | 9 | 26181 | 47.05 | 136868.45 | 209 | 0 | 60 | 2909 | 88 | 2909 | 16 | 0 | 80 | 0 | 275 | 0 | 739525.98 | 46386623.1 | 254.22 | 15945.9
26 | Sahiwal-2nd | Arif Road | Urban | 6321 | 16 | 4.8 | 30340.8 | 20 | 31.2 | 236658.24 | 31.2 | 236658.24 | 0 | 0 | 0 | 0 | 36 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 266999.04 | 14290516.8 | 42.24 | 2260.8
27 | Sahiwal-2nd | Wapda Colony | Urban | 116 | 6 | 1.8 | 208.8 | 9 | 13.2 | 1837.44 | 13.2 | 1837.44 | 6 | 696 | 26.35 | 3056.6 | 15 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 2742.24 | 294268.8 | 23.64 | 2536.8
28 | Sahiwal-2nd | City | Urban | 4531 | 69 | 20.7 | 93791.7 | 86 | 134.3 | 730215.96 | 134.3 | 730215.96 | 8 | 36248 | 41.1 | 186224.1 | 155 | 0 | 60 | 4531 | 88 | 4531 | 16 | 0 | 80 | 0 | 275 | 0 | 860255.66 | 55267778.7 | 189.86 | 12197.7
29 | Sahiwal-2nd | City 2 | Urban | 4475 | 97 | 29.1 | 130222.5 | 126 | 193.9 | 1041243 | 193.9 | 1041243 | 22 | 98450 | 108.35 | 484866.25 | 223 | 0 | 60 | 4475 | 88 | 4475 | 16 | 4475 | 80 | 4475 | 275 | 0 | 1269915.5 | 91957222.5 | 283.78 | 20549.1
30 | Sahiwal-2nd | Industrial Estate | Urban | 3978 | 100 | 30 | 119340 | 90 | 160 | 763776 | 160 | 763776 | 8 | 31824 | 46.05 | 183186.9 | 190 | 0 | 60 | 3978 | 88 | 3978 | 16 | 0 | 80 | 0 | 275 | 0 | 914940 | 57175794 | 230 | 14373
31 | Sahiwal-2nd | Jahaz Ground | Urban | 2523 | 38 | 11.4 | 28762.2 | 10 | 36.6 | 110810.16 | 36.6 | 110810.16 | 32 | 80736 | 47.16 | 118984.68 | 48 | 0 | 60 | 0 | 88 | 0 | 16 | 2523 | 80 | 0 | 275 | 0 | 220308.36 | 13873977 | 87.32 | 5499
32 | Sahiwal-2nd | Police Line | Urban | 2075 | 38 | 11.4 | 23655 | 9 | 35.6 | 88644 | 35.6 | 88644 | 44 | 91300 | 99.28 | 206006 | 47 | 0 | 60 | 0 | 88 | 0 | 16 | 2075 | 80 | 2075 | 275 | 0 | 203599 | 17749965 | 98.12 | 8554.2
33 | Chichawatni | City | Urban | 6119 | 70 | 21 | 128499 | 13 | 62 | 455253.6 | 62 | 455253.6 | 125 | 764875 | 125 | 764875 | 82 | 1 | 60 | 6119 | 88 | 0 | 16 | 6119 | 80 | 6119 | 275 | 0 | 1348627.6 | 73593213 | 220.4 | 12027
34 | Chichawatni | Muhammad Abad | Urban | 5305 | 51 | 15.3 | 81166.5 | 8 | 43.7 | 278194.2 | 43.7 | 278194.2 | 90 | 477450 | 100.03 | 530659.15 | 58 | 1 | 60 | 5305 | 88 | 0 | 16 | 5305 | 80 | 5305 | 275 | 0 | 836810.7 | 48774700.5 | 157.74 | 9194.1
35 | Chichawatni | Industrial | Urban | 9560 | 202 | 60.6 | 579336 | 7 | 148.4 | 1702444.8 | 148.4 | 1702444.8 | 84 | 803040 | 118 | 1128080 | 208 | 1 | 60 | 9560 | 88 | 9560 | 16 | 9560 | 80 | 9560 | 275 | 0 | 3084820.8 | 171569496 | 322.68 | 17946.6
36 | Chichawatni | New City | Urban | 6031 | 40 | 12 | 72372 | 21 | 49 | 354622.8 | 49 | 354622.8 | 81 | 488511 | 92.03 | 555032.93 | 60 | 1 | 60 | 6031 | 88 | 0 | 16 | 6031 | 80 | 6031 | 275 | 0 | 915505.8 | 54796459.8 | 151.8 | 9085.8
37 | Chichawatni | Rai Kot | Urban | 6006 | 65 | 19.5 | 117117 | 7 | 52.5 | 378378 | 52.5 | 378378 | 82 | 492492 | 87 | 522522 | 71 | 1 | 60 | 6006 | 88 | 0 | 16 | 6006 | 80 | 6006 | 275 | 0 | 987987 | 54405351 | 164.5 | 9058.5
38 | Arif Wala | Gulshane Iqbal | Urban | 4914 | 344 | 103.2 | 507124.8 | 65 | 305.8 | 1803241.44 | 305.8 | 1803241.44 | 74 | 363636 | 29.5 | 144963 | 409 | 0 | 60 | 4914 | 88 | 4914 | 16 | 4914 | 80 | 0 | 275 | 0 | 2674002.24 | 118413640.8 | 544.16 | 24097.2
39 | Arif Wala | Power House | Urban | 4133 | 317 | 95.1 | 393048.3 | 40 | 261.9 | 1298919.24 | 261.9 | 1298919.24 | 65 | 268645 | 30.4 | 125643.2 | 357 | 0 | 60 | 4133 | 88 | 4133 | 16 | 4133 | 80 | 0 | 275 | 0 | 1960612.54 | 86652891.3 | 474.38 | 20966.1
40 | Arif Wala | Jinnah | Urban | 5217 | 170 | 51 | 266067 | 34 | 153 | 957841.2 | 153 | 957841.2 | 56 | 292152 | 24.1 | 125729.7 | 204 | 0 | 60 | 5217 | 88 | 5217 | 16 | 5217 | 80 | 0 | 275 | 0 | 1516060.2 | 65812455 | 290.6 | 12615
41 | Arif Wala | City | Urban | 8104 | 349 | 104.7 | 848488.8 | 48 | 292.3 | 2842559.04 | 292.3 | 2842559.04 | 87 | 705048 | 46.3 | 375215.2 | 397 | 0 | 60 | 8104 | 88 | 8104 | 16 | 8104 | 80 | 0 | 275 | 0 | 4396095.84 | 195611920.8 | 542.46 | 24137.7
42 | Pakpattan | Aziz Makki | Urban | 2637 | 239 | 71.7 | 189072.9 | 16 | 183.3 | 580034.52 | 183.3 | 580034.52 | 75 | 197775 | 12.08 | 31854.96 | 255 | 0 | 60 | 2637 | 88 | 2637 | 16 | 2637 | 80 | 0 | 275 | 0 | 966882.42 | 37280587.5 | 366.66 | 14137.5
43 | Pakpattan | Baba Dost Muhammad | Urban | 7425 | 76 | 22.8 | 169290 | 4 | 57.2 | 509652 | 57.2 | 509652 | 7 | 51975 | 38.05 | 282521.25 | 80 | 0 | 60 | 7425 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 730917 | 48038265 | 98.44 | 6469.8
44 | Pakpattan | Power House | Urban | 7746 | 389 | 116.7 | 903958.2 | 13 | 285.3 | 2651920.56 | 285.3 | 2651920.56 | 71 | 549966 | 270.07 | 2091962.22 | 402 | 0 | 60 | 7746 | 88 | 7746 | 16 | 7746 | 80 | 7746 | 275 | 0 | 4105844.76 | 287344841.4 | 530.06 | 37095.9
45 | Pakpattan | Farid Nagar | Urban | 2790 | 196 | 58.8 | 164052 | 14 | 151.2 | 506217.6 | 151.2 | 506217.6 | 57 | 159030 | 248.35 | 692896.5 | 210 | 0 | 60 | 2790 | 88 | 2790 | 16 | 2790 | 80 | 2790 | 275 | 0 | 829299.6 | 72439002 | 297.24 | 25963.8
46 | Pakpattan | Al-Farid | Urban | 6016 | 252 | 75.6 | 454809.6 | 7 | 183.4 | 1324001.28 | 183.4 | 1324001.28 | 115 | 691840 | 414.51 | 2493692.16 | 259 | 0 | 60 | 6016 | 88 | 6016 | 16 | 6016 | 80 | 6016 | 275 | 0 | 2470650.88 | 230426035.2 | 410.68 | 38302.2
47 | Pakpattan | Mubashar Shaheed | Urban | 3144 | 216 | 64.8 | 203731.2 | 10 | 161.2 | 608175.36 | 161.2 | 608175.36 | 17 | 53448 | 328 | 1031232 | 226 | 0 | 60 | 3144 | 88 | 3144 | 16 | 3144 | 80 | 3144 | 275 | 0 | 865354.56 | 98975635.2 | 275.24 | 31480.8
48 | Pakpattan | City | Urban | 9247 | 310 | 93 | 859971 | 11 | 228 | 2529979.2 | 228 | 2529979.2 | 62 | 573314 | 224.35 | 2074564.45 | 321 | 0 | 60 | 9247 | 88 | 9247 | 16 | 9247 | 80 | 9247 | 275 | 0 | 3963264.2 | 278852532 | 428.6 | 30156
|  | TOTAL |  | 177622 | 3929 | 1307.1 | 6523701 | 1097 | 4202.9 | 24430906.8 | 4202.9 | 24430906.8 | 2070 | 11010704 | 4225.55 | 12955735.48 | 5503 | 7 | 60 | 152045 | 88 | 95751 | 16 | 142750 | 80 | 78609 | 275 | 0 | 41965311.8 | 2262769639.8 | 236.2619 | 12739.242

## 400-220 (Urban) RYKhan
Statement of 400/220 V MEPCO Consumers For 2020-21
R.Y Khan Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | R.Y.Khan | City | Urban | 3940 | 20 | 6 | 23640 | 20 | 34 | 160752 | 34 | 160752 | 12 | 47280 | 41 | 161540 | 40 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 231672 | 19408440 | 58.8 | 4926
2 | R.Y.Khan | Circular | Urban | 4907 | 3 | 0.9 | 4416.3 | 3 | 5.1 | 30030.84 | 5.1 | 30030.84 | 15 | 73605 | 56 | 274792 | 6 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 108052.14 | 18302619.3 | 22.02 | 3729.9
3 | R.Y.Khan | Allama Iqbal | Urban | 4493 | 35 | 10.5 | 47176.5 | 35 | 59.5 | 320800.2 | 59.5 | 320800.2 | 16 | 71888 | 57 | 256101 | 70 | 0 | 60 | 4493 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 439864.7 | 34755601.5 | 97.9 | 7735.5
4 | R.Y.Khan | Qaid-e-Azam | Urban | 3996 | 30 | 9 | 35964 | 30 | 51 | 244555.2 | 51 | 244555.2 | 14 | 55944 | 45 | 179820 | 60 | 0 | 60 | 3996 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 336463.2 | 25570404 | 84.2 | 6399
5 | R.Y.Khan | Millat | Urban | 8377 | 12 | 3.6 | 30157.2 | 12 | 20.4 | 205068.96 | 20.4 | 205068.96 | 18 | 150786 | 50 | 418850 | 24 | 0 | 60 | 0 | 88 | 0 | 16 | 8377 | 80 | 0 | 275 | 0 | 386012.16 | 37525609.2 | 46.08 | 4479.6
6 | R.Y.Khan | S/Town | Urban | 5178 | 28 | 8.4 | 43495.2 | 28 | 47.6 | 295767.36 | 47.6 | 295767.36 | 19 | 98382 | 60 | 310680 | 56 | 0 | 60 | 5178 | 88 | 0 | 16 | 5178 | 80 | 0 | 275 | 0 | 437644.56 | 36517327.2 | 84.52 | 7052.4
7 | R.Y.Khan | Industrial-I | Urban | 9015 | 28 | 8.4 | 75726 | 28 | 47.6 | 514936.8 | 47.6 | 514936.8 | 15 | 135225 | 60 | 540900 | 56 | 0 | 60 | 9015 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 725887.8 | 63577386 | 80.52 | 7052.4
8 | R.Y.Khan | Gulshan | Urban | 8609 | 35 | 10.5 | 90394.5 | 35 | 59.5 | 614682.6 | 59.5 | 614682.6 | 12 | 103308 | 41 | 352969 | 70 | 0 | 60 | 8609 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 808385.1 | 58330279.5 | 93.9 | 6775.5
9 | R.Y.Khan | Industrial-II | Urban | 5553 | 25 | 7.5 | 41647.5 | 25 | 42.5 | 283203 | 42.5 | 283203 | 15 | 83295 | 61 | 338733 | 50 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 408145.5 | 37441102.5 | 73.5 | 6742.5
10 | R.Y.Khan | Rafiqabad | Urban | 2176 | 25 | 7.5 | 16320 | 25 | 42.5 | 110976 | 42.5 | 110976 | 15 | 32640 | 61 | 132736 | 50 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 159936 | 14671680 | 73.5 | 6742.5
11 | R.Y.Khan | Factory Area | Urban | 1739 | 8 | 2.4 | 4173.6 | 8 | 13.6 | 28380.48 | 13.6 | 28380.48 | 15 | 26085 | 65 | 113035 | 16 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 58639.08 | 8497449.6 | 33.72 | 4886.4
12 | R.Y.Khan | Rehman Colony | Urban | 1503 | 7 | 2.1 | 3156.3 | 7 | 11.9 | 21462.84 | 11.9 | 21462.84 | 11 | 16533 | 44 | 66132 | 14 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 41152.14 | 5265159.3 | 27.38 | 3503.1
13 | R.Y.Khan | Bahishti | Urban | 8317 | 60 | 18 | 149706 | 60 | 102 | 1018000.8 | 102 | 1018000.8 | 21 | 174657 | 81 | 673677 | 120 | 0 | 60 | 8317 | 88 | 8317 | 16 | 8317 | 80 | 8317 | 275 | 0 | 1342363.8 | 101949786 | 161.4 | 12258
14 | R.Y.Khan | Aziz Abad | Urban | 5846 | 65 | 19.5 | 113997 | 65 | 110.5 | 775179.6 | 110.5 | 775179.6 | 18 | 105228 | 87 | 508602 | 130 | 0 | 60 | 5846 | 88 | 5846 | 16 | 5846 | 80 | 5846 | 275 | 0 | 994404.6 | 77368887 | 170.1 | 13234.5
15 | R.Y.Khan | Sakhi Sarwar | Urban | 9627 | 65 | 19.5 | 187726.5 | 65 | 110.5 | 1276540.2 | 110.5 | 1276540.2 | 18 | 173286 | 78 | 750906 | 130 | 0 | 60 | 9627 | 88 | 9627 | 16 | 9627 | 80 | 0 | 275 | 0 | 1637552.7 | 122209951.5 | 170.1 | 12694.5
16 | R.Y.Khan | New S/Town | Urban | 5976 | 48 | 14.4 | 86054.4 | 12 | 45.6 | 327006.72 | 45.6 | 327006.72 | 15 | 89640 | 41 | 245016 | 60 | 0 | 60 | 5976 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 502701.12 | 34579526.4 | 84.12 | 5786.4
17 | R.Y.Khan | Model Town | Urban | 7874 | 60 | 18 | 141732 | 15 | 57 | 538581.6 | 57 | 538581.6 | 15 | 118110 | 39 | 307086 | 75 | 0 | 60 | 7874 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 798423.6 | 51165252 | 101.4 | 6498
18 | R.Y.Khan | Jinnah | Urban | 6808 | 10 | 3 | 20424 | 20 | 27 | 220579.2 | 27 | 220579.2 | 24 | 163392 | 60 | 408480 | 30 | 0 | 60 | 0 | 88 | 0 | 16 | 6808 | 80 | 0 | 275 | 0 | 404395.2 | 37804824 | 59.4 | 5553
19 | Khanpur | City | Urban | 5415 | 120 | 36 | 194940 | 20 | 104 | 675792 | 104 | 675792 | 25 | 135375 | 99 | 536085 | 140 | 0 | 60 | 5415 | 88 | 5415 | 16 | 5415 | 80 | 5415 | 275 | 0 | 1006107 | 73297440 | 185.8 | 13536
20 | Khanpur | Jinnah | Urban | 7392 | 110 | 33 | 243936 | 15 | 92 | 816076.8 | 92 | 816076.8 | 24 | 177408 | 71 | 524832 | 125 | 0 | 60 | 7392 | 88 | 7392 | 16 | 7392 | 80 | 0 | 275 | 0 | 1237420.8 | 81186336 | 167.4 | 10983
21 | Khanpur | Model Town | Urban | 7523 | 110 | 33 | 248259 | 20 | 97 | 875677.2 | 97 | 875677.2 | 27 | 203121 | 60 | 451380 | 130 | 0 | 60 | 7523 | 88 | 7523 | 16 | 7523 | 80 | 0 | 275 | 0 | 1327057.2 | 80368209 | 176.4 | 10683
22 | Khanpur | Fareedi | Urban | 6534 | 120 | 36 | 235224 | 20 | 104 | 815443.2 | 104 | 815443.2 | 33 | 215622 | 99 | 646866 | 140 | 0 | 60 | 6534 | 88 | 6534 | 16 | 6534 | 80 | 6534 | 275 | 0 | 1266289.2 | 88444224 | 193.8 | 13536
23 | Khanpur | Akhtar Abad | Urban | 5136 | 120 | 36 | 184896 | 25 | 109 | 671788.8 | 109 | 671788.8 | 27 | 138672 | 89 | 457104 | 145 | 0 | 60 | 5136 | 88 | 5136 | 16 | 5136 | 80 | 5136 | 275 | 0 | 995356.8 | 68288256 | 193.8 | 13296
24 | Khanpur | Saddar Bazar | Urban | 7500 | 130 | 39 | 292500 | 20 | 111 | 999000 | 111 | 999000 | 42 | 315000 | 98 | 735000 | 150 | 0 | 60 | 7500 | 88 | 7500 | 16 | 7500 | 80 | 7500 | 275 | 0 | 1606500 | 104917500 | 214.2 | 13989
25 | Liaqat Pur | City Liaqat pur | Urban | 9852 | 70 | 21 | 206892 | 60 | 109 | 1288641.6 | 109 | 1288641.6 | 12 | 118224 | 25 | 246300 | 129 | 1 | 60 | 9852 | 88 | 9852 | 16 | 0 | 80 | 0 | 275 | 0 | 1613757.6 | 92717172 | 163.8 | 9411
26 | Liaqat Pur | Kachi Mandi | Urban | 6953 | 80 | 24 | 166872 | 60 | 116 | 967857.6 | 116 | 967857.6 | 11 | 76483 | 35 | 243355 | 140 | 0 | 60 | 6953 | 88 | 6953 | 16 | 0 | 80 | 0 | 275 | 0 | 1211212.6 | 73173372 | 174.2 | 10524
27 | Sadiqabad | AJMAL BAGH | Urban | 2719 | 45 | 13.5 | 36706.5 | 15 | 46.5 | 151720.2 | 46.5 | 151720.2 | 29 | 78851 | 99 | 269181 | 60 | 0 | 60 | 2719 | 88 | 0 | 16 | 2719 | 80 | 2719 | 275 | 0 | 267277.7 | 25364191.5 | 98.3 | 9328.5
28 | Sadiqabad | CITY NO.1 | Urban | 7424 | 25 | 7.5 | 55680 | 15 | 32.5 | 289536 | 32.5 | 289536 | 24 | 178176 | 68 | 504832 | 39 | 1 | 60 | 0 | 88 | 0 | 16 | 7424 | 80 | 0 | 275 | 0 | 523392 | 47829120 | 70.5 | 6442.5
29 | Sadiqabad | JOHAR TOWN | Urban | 8327 | 70 | 21 | 174867 | 8 | 57 | 569566.8 | 57 | 569566.8 | 23 | 191521 | 80 | 666160 | 78 | 0 | 60 | 8327 | 88 | 0 | 16 | 8327 | 80 | 0 | 275 | 0 | 935954.8 | 74668209 | 112.4 | 8967
30 | Sadiqabad | JINNAH TOWN | Urban | 7546 | 99 | 29.7 | 224116.2 | 20 | 89.3 | 808629.36 | 89.3 | 808629.36 | 34 | 256564 | 97 | 731962 | 119 | 0 | 60 | 7546 | 88 | 7546 | 16 | 7546 | 80 | 7546 | 275 | 0 | 1289309.56 | 93107830.2 | 170.86 | 12338.7
31 | Sadiqabad | Old MANTHAR | Urban | 8092 | 100 | 30 | 242760 | 12 | 82 | 796252.8 | 82 | 796252.8 | 31 | 250852 | 66 | 534072 | 112 | 0 | 60 | 8092 | 88 | 8092 | 16 | 8092 | 80 | 0 | 275 | 0 | 1289864.8 | 80547768 | 159.4 | 9954
32 | Sadiqabad | Noor Wala | Urban | 5002 | 36 | 10.8 | 54021.6 | 20 | 45.2 | 271308.48 | 45.2 | 271308.48 | 28 | 140056 | 75 | 375150 | 55 | 1 | 60 | 5002 | 88 | 0 | 16 | 5002 | 80 | 0 | 275 | 0 | 465386.08 | 38949573.6 | 93.04 | 7786.8
33 | Sadiqabad | NEW SATELLITE TOWN | Urban | 3624 | 40 | 12 | 43488 | 21 | 49 | 213091.2 | 49 | 213091.2 | 25 | 90600 | 78 | 282672 | 60 | 1 | 60 | 3624 | 88 | 0 | 16 | 3624 | 80 | 0 | 275 | 0 | 347179.2 | 29876256 | 95.8 | 8244
34 | Sadiqabad | SADIQ Feeder | Urban | 4855 | 36 | 10.8 | 52434 | 35 | 60.2 | 350725.2 | 60.2 | 350725.2 | 35 | 169925 | 105 | 509775 | 71 | 0 | 60 | 4855 | 88 | 0 | 16 | 4855 | 80 | 4855 | 275 | 0 | 573084.2 | 51787314 | 118.04 | 10666.8
35 | Sadiqabad | NISHTER | Urban | 4493 | 64 | 19.2 | 86265.6 | 25 | 69.8 | 376333.68 | 69.8 | 376333.68 | 41 | 184213 | 80 | 359440 | 88 | 1 | 60 | 4493 | 88 | 0 | 16 | 4493 | 80 | 0 | 275 | 0 | 646812.28 | 44405217.6 | 143.96 | 9883.2
36 | Sadiqabad | SETTLITE TOWN | Urban | 6463 | 98 | 29.4 | 190012.2 | 15 | 83.6 | 648368.16 | 83.6 | 648368.16 | 35 | 226205 | 89 | 575207 | 111 | 2 | 60 | 6463 | 88 | 6463 | 16 | 6463 | 80 | 6463 | 275 | 0 | 1064585.36 | 73984546.2 | 164.72 | 11447.4
37 | Sadiqabad | MODEL TOWN | Urban | 6804 | 55 | 16.5 | 112266 | 8 | 46.5 | 379663.2 | 46.5 | 379663.2 | 35 | 238140 | 83 | 564732 | 62 | 1 | 60 | 6804 | 88 | 0 | 16 | 6804 | 80 | 6804 | 275 | 0 | 730069.2 | 57000510 | 107.3 | 8377.5
38 | Sadiqabad | CITY (F.NO.11) | Urban | 5450 | 120 | 36 | 196200 | 17 | 101 | 660540 | 101 | 660540 | 21 | 114450 | 45 | 245250 | 135 | 2 | 60 | 5450 | 88 | 5450 | 16 | 5450 | 80 | 0 | 275 | 0 | 971190 | 54936000 | 178.2 | 10080
39 | Sadiqabad | MODEL CITY | Urban | 380 | 8 | 2.4 | 912 | 7 | 12.6 | 5745.6 | 12.6 | 5745.6 | 39 | 14820 | 98 | 37240 | 15 | 0 | 60 | 0 | 88 | 0 | 16 | 380 | 80 | 380 | 275 | 0 | 21477.6 | 2581872 | 56.52 | 6794.4
40 | Sadiqabad | MODEL AVENUE | Urban | 95 | 15 | 4.5 | 427.5 | 11 | 21.5 | 2451 | 21.5 | 2451 | 61 | 5795 | 132 | 12540 | 26 | 0 | 60 | 0 | 88 | 0 | 16 | 95 | 80 | 95 | 275 | 0 | 8673.5 | 900742.5 | 91.3 | 9481.5
|  | TOTAL |  | 231418 | 2220 | 666 | 4359155.1 | 951 | 2505 | 19618262.28 | 2505 | 19618262.28 | 889 | 5233562 | 2666 | 15536650 | 3161 | 10 | 60 | 188611 | 88 | 107646 | 16 | 154832 | 80 | 67515 | 275 | 0 | 29210979.38 | 2122372202.1 | 126.226 | 9171.163

## 400-220 (Urban) M-Garh
Statement of 400/220 V MEPCO Consumers For 2020-21
Muzaffargarh Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | M/Garh | Power House | Urban | 6307 | 180 | 54 | 340578 | 40 | 166 | 1256354.4 | 166 | 1256354.4 | 120 | 756840 | 160 | 1009120 | 220 | 0 | 60 | 6307 | 88 | 6307 | 16 | 6307 | 80 | 6307 | 275 | 0 | 2353772.4 | 136950198 | 373.2 | 21714
2 | M/Garh | Taliri (TPS) | Urban | 9754 | 250 | 75 | 731550 | 50 | 225 | 2633580 | 225 | 2633580 | 110 | 1072940 | 18 | 175572 | 300 | 0 | 60 | 9754 | 88 | 9754 | 16 | 9754 | 80 | 9754 | 275 | 0 | 4438070 | 170743770 | 455 | 17505
3 | M/Garh | Muzaffargarh | Urban | 5439 | 170 | 51 | 277389 | 45 | 164 | 1070395.2 | 164 | 1070395.2 | 80 | 435120 | 110 | 598290 | 215 | 0 | 60 | 5439 | 88 | 5439 | 16 | 5439 | 80 | 5439 | 275 | 0 | 1782904.2 | 100953279 | 327.8 | 18561
4 | M/Garh | Turkish Colony | Urban | 1338 | 72 | 21.6 | 28900.8 | 9 | 59.4 | 95372.64 | 59.4 | 95372.64 | 6 | 8028 | 7 | 9366 | 81 | 0 | 60 | 1338 | 88 | 0 | 16 | 1338 | 80 | 1338 | 275 | 0 | 132301.44 | 6371020.8 | 98.88 | 4761.6
5 | M/Garh | Yadgar Club | Urban | 4836 | 120 | 36 | 174096 | 26 | 110 | 638352 | 110 | 638352 | 65 | 314340 | 110 | 531960 | 146 | 0 | 60 | 4836 | 88 | 4836 | 16 | 4836 | 80 | 4836 | 275 | 0 | 1126788 | 70741008 | 233 | 14628
6 | M/Garh | Khursheed Abad | Urban | 4301 | 76 | 22.8 | 98062.8 | 48 | 101.2 | 522313.44 | 101.2 | 522313.44 | 50 | 215050 | 50 | 215050 | 124 | 0 | 60 | 4301 | 88 | 4301 | 16 | 4301 | 80 | 4301 | 275 | 0 | 835426.24 | 44535994.8 | 194.24 | 10354.8
7 | Kot Addu | Kot Addu City-I | Urban | 6478 | 34 | 10.2 | 66075.6 | 18 | 41.8 | 324936.48 | 41.8 | 324936.48 | 86 | 557108 | 122 | 790316 | 52 | 0 | 60 | 6478 | 88 | 0 | 16 | 6478 | 80 | 6478 | 275 | 0 | 948120.08 | 67113375.6 | 146.36 | 10360.2
8 | Kot Addu | Kot Addu City-II | Urban | 4221 | 50 | 15 | 63315 | 22 | 57 | 288716.4 | 57 | 288716.4 | 77 | 325017 | 121 | 510741 | 72 | 0 | 60 | 4221 | 88 | 0 | 16 | 4221 | 80 | 4221 | 275 | 0 | 677048.4 | 48157389 | 160.4 | 11409
9 | Kot Addu | D.D. Panah | Urban | 9756 | 57 | 17.1 | 166827.6 | 31 | 70.9 | 830040.48 | 70.9 | 830040.48 | 128 | 1248768 | 208 | 2029248 | 88 | 0 | 60 | 9756 | 88 | 0 | 16 | 9756 | 80 | 9756 | 275 | 0 | 2245636.08 | 172057791.6 | 230.18 | 17636.1
10 | Kot Addu | College Road | Urban | 11549 | 89 | 26.7 | 308358.3 | 38 | 100.3 | 1390037.64 | 100.3 | 1390037.64 | 84 | 970116 | 178 | 2055722 | 127 | 0 | 60 | 11549 | 88 | 11549 | 16 | 11549 | 80 | 11549 | 275 | 0 | 2668511.94 | 207670653.3 | 231.06 | 17981.7
11 | Layyah | Eid Gah | Urban | 8233 | 97 | 29.1 | 239580.3 | 36 | 103.9 | 1026490.44 | 103.9 | 1026490.44 | 40 | 329320 | 115 | 946795 | 133 | 0 | 60 | 8233 | 88 | 8233 | 16 | 8233 | 80 | 8233 | 275 | 0 | 1595390.74 | 119115867.3 | 193.78 | 14468.1
12 | Layyah | Sugar Mills | Urban | 1925 | 63 | 18.9 | 36382.5 | 10 | 54.1 | 124971 | 54.1 | 124971 | 20 | 38500 | 60 | 115500 | 73 | 0 | 60 | 1925 | 88 | 0 | 16 | 1925 | 80 | 1925 | 275 | 0 | 199853.5 | 14537407.5 | 103.82 | 7551.9
13 | Layyah | City-I | Urban | 7758 | 74 | 22.2 | 172227.6 | 25 | 76.8 | 714977.28 | 76.8 | 714977.28 | 43 | 333594 | 87 | 674946 | 99 | 0 | 60 | 7758 | 88 | 7758 | 16 | 7758 | 80 | 7758 | 275 | 0 | 1220798.88 | 83912079.6 | 157.36 | 10816.2
14 | Layyah | City-II | Urban | 6896 | 50 | 15 | 103440 | 18 | 53 | 438585.6 | 53 | 438585.6 | 37 | 255152 | 72 | 496512 | 68 | 0 | 60 | 6896 | 88 | 0 | 16 | 6896 | 80 | 6896 | 275 | 0 | 797177.6 | 56416176 | 115.6 | 8181
15 | Layyah | City-III | Urban | 4753 | 73 | 21.9 | 104090.7 | 23 | 74.1 | 422636.76 | 74.1 | 422636.76 | 47 | 223391 | 123 | 584619 | 96 | 0 | 60 | 4753 | 88 | 4753 | 16 | 4753 | 80 | 4753 | 275 | 0 | 750118.46 | 60747617.7 | 157.82 | 12780.9
16 | Layyah | Lal Eason | Urban | 6886 | 209 | 62.7 | 431752.2 | 6 | 152.3 | 1258485.36 | 152.3 | 1258485.36 | 3 | 20658 | 12 | 82632 | 215 | 0 | 60 | 6886 | 88 | 6886 | 16 | 6886 | 80 | 6886 | 275 | 0 | 1710895.56 | 81762298.2 | 248.46 | 11873.7
17 | Layyah | City-II Lal Eason | Urban | 3673 | 125 | 37.5 | 137737.5 | 11 | 98.5 | 434148.6 | 98.5 | 434148.6 | 1 | 3673 | 04 | 14692 | 136 | 0 | 60 | 3673 | 88 | 3673 | 16 | 3673 | 80 | 3673 | 275 | 0 | 575559.1 | 27343648.5 | 156.7 | 7444.5
18 | Layyah | Fatehpur | Urban | 10137 | 140 | 42 | 425754 | 30 | 128 | 1557043.2 | 128 | 1557043.2 | 2 | 20274 | 11 | 111507 | 170 | 0 | 60 | 10137 | 88 | 10137 | 16 | 10137 | 80 | 10137 | 275 | 0 | 2003071.2 | 101390274 | 197.6 | 10002
19 | Layyah | Chowk Azam-I | Urban | 9423 | 144 | 43.2 | 407073.6 | 24 | 124.8 | 1411188.48 | 124.8 | 1411188.48 | 29 | 273267 | 53 | 499419 | 168 | 0 | 60 | 9423 | 88 | 9423 | 16 | 9423 | 80 | 9423 | 275 | 0 | 2091529.08 | 115857669.6 | 221.96 | 12295.2
20 | Layyah | Chowk Azam-II | Urban | 8404 | 182 | 54.6 | 458858.4 | 30 | 157.4 | 1587347.52 | 157.4 | 1587347.52 | 35 | 294140 | 51 | 428604 | 212 | 0 | 60 | 8404 | 88 | 8404 | 16 | 8404 | 80 | 8404 | 275 | 0 | 2340345.92 | 122333666.4 | 278.48 | 14556.6
21 | Layyah | Multan Garden City | Urban | 62 | 10 | 3 | 186 | 14 | 21 | 1562.4 | 21 | 1562.4 | 7 | 434 | 21 | 1302 | 24 | 0 | 60 | 0 | 88 | 0 | 16 | 62 | 80 | 62 | 275 | 0 | 2182.4 | 172422 | 35.2 | 2781
22 | Alipur | City (T/W-5) | Urban | 9343 | 225 | 67.5 | 630652.5 | 35 | 192.5 | 2158233 | 192.5 | 2158233 | 245 | 2289035 | 375 | 3503625 | 260 | 0 | 60 | 9343 | 88 | 9343 | 16 | 9343 | 80 | 9343 | 275 | 0 | 5077920.5 | 341603437.5 | 543.5 | 36562.5
23 | Alipur | Rohillanwali | Urban | 10017 | 597 | 179.1 | 1794044.7 | 63 | 480.9 | 5780610.36 | 480.9 | 5780610.36 | 63 | 631071 | 208 | 2083536 | 660 | 0 | 60 | 10017 | 88 | 10017 | 16 | 10017 | 80 | 10017 | 275 | 0 | 8205726.06 | 477230915.7 | 819.18 | 47642.1
24 | Alipur | Rohillanwali-II | Urban | 6088 | 583 | 174.9 | 1064791.2 | 64 | 472.1 | 3448973.76 | 472.1 | 3448973.76 | 117 | 712296 | 19 | 115672 | 647 | 0 | 60 | 6088 | 88 | 6088 | 16 | 6088 | 80 | 6088 | 275 | 0 | 5226060.96 | 217073119.2 | 858.42 | 35655.9
25 | Alipur | City-I Alipur | Urban | 5867 | 227 | 68.1 | 399542.7 | 40 | 198.9 | 1400335.56 | 198.9 | 1400335.56 | 229 | 1343543 | 363 | 2129721 | 267 | 0 | 60 | 5867 | 88 | 5867 | 16 | 5867 | 80 | 5867 | 275 | 0 | 3143421.26 | 213002021.7 | 535.78 | 36305.1
26 | Alipur | City-II Alipur | Urban | 7038 | 201 | 60.3 | 424391.4 | 43 | 183.7 | 1551456.72 | 183.7 | 1551456.72 | 186 | 1309068 | 261 | 1836918 | 244 | 0 | 60 | 7038 | 88 | 7038 | 16 | 7038 | 80 | 7038 | 275 | 0 | 3284916.12 | 204575657.4 | 466.74 | 29067.3
27 | Alipur | Al-Manan Garden | Urban | 13 | 3 | 0.9 | 11.7 | 2 | 4.1 | 63.96 | 4.1 | 63.96 | 13 | 169 | 46 | 598 | 5 | 0 | 60 | 0 | 88 | 0 | 16 | 13 | 80 | 13 | 275 | 0 | 244.66 | 39752.7 | 18.82 | 3057.9
|  | TOTAL |  | 157577 | 230 | 1101 | 8261724.3 | 109 | 3285 | 29415352.44 | 3285 | 29415352.44 | 375 | 11328132 | 629 | 17584746 | 4386 | 0 | 60 | 157515 | 88 | 126901 | 16 | 157577 | 80 | 157577 | 275 | 0 | 49005208.74 | 2844791079.3 | 310.9921 | 18053.3395

## 400-220 (Urban) B_Nagar
Statement of 400/220 V MEPCO Consumers For 2020-21
Bahawal Nagar Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | B/Nagar | City I | Urban | 8045 | 82 | 24.6 | 197907 | 13 | 70.4 | 679641.6 | 70.4 | 679641.6 | 53 | 426385 | 90 | 724050 | 95 | 0 | 60 | 8045 | 88 | 0 | 16 | 8045 | 80 | 8045 | 275 | 0 | 1303933.6 | 84815217 | 162.08 | 10542.6
2 | B/Nagar | City II | Urban | 5602 | 114 | 34.2 | 191588.4 | 15 | 94.8 | 637283.52 | 94.8 | 637283.52 | 35 | 196070 | 49 | 274498 | 129 | 0 | 60 | 5602 | 88 | 5602 | 16 | 5602 | 80 | 5602 | 275 | 0 | 1024941.92 | 55281656.4 | 182.96 | 9868.2
3 | B/Nagar | Nizam Pura | Urban | 6207 | 80 | 24 | 148968 | 11 | 67 | 499042.8 | 67 | 499042.8 | 176 | 1092432 | 157 | 974499 | 91 | 0 | 60 | 6207 | 88 | 0 | 16 | 6207 | 80 | 6207 | 275 | 0 | 1740442.8 | 88859412 | 280.4 | 14316
4 | B/Nagar | Chishtian Road | Urban | 2896 | 37 | 11.1 | 32145.6 | 7 | 32.9 | 114334.08 | 32.9 | 114334.08 | 36 | 104256 | 82 | 237472 | 44 | 0 | 60 | 0 | 88 | 0 | 16 | 2896 | 80 | 2896 | 275 | 0 | 250735.68 | 21204801.6 | 86.58 | 7322.1
5 | B/Nagar | Nawab Sadiq | Urban | 2506 | 99 | 29.7 | 74428.2 | 8 | 77.3 | 232456.56 | 77.3 | 232456.56 | 43 | 107758 | 107 | 268142 | 107 | 0 | 60 | 2506 | 88 | 2506 | 16 | 2506 | 80 | 2506 | 275 | 0 | 414642.76 | 30259198.2 | 165.46 | 12074.7
6 | B/Nagar | New City H. Scheme | Urban | 237 | 46 | 13.8 | 3270.6 | 8 | 40.2 | 11432.88 | 40.2 | 11432.88 | 9 | 2133 | 36 | 8532 | 54 | 0 | 60 | 237 | 88 | 0 | 16 | 0 | 80 | 237 | 275 | 0 | 16836.48 | 1207704.6 | 71.04 | 5095.8
7 | B/Nagar | Nazir Shaheed | Urban | 1882 | 37 | 11.1 | 20890.2 | 7 | 32.9 | 74301.36 | 32.9 | 74301.36 | 28 | 52696 | 65 | 122330 | 44 | 0 | 60 | 0 | 88 | 0 | 16 | 1882 | 80 | 1882 | 275 | 0 | 147887.56 | 11860552.2 | 78.58 | 6302.1
8 | B/Nagar | Canal | Urban | 8459 | 152 | 45.6 | 385730.4 | 16 | 122.4 | 1242457.92 | 122.4 | 1242457.92 | 96 | 812064 | 125 | 1057375 | 168 | 0 | 60 | 8459 | 88 | 8459 | 16 | 8459 | 80 | 8459 | 275 | 0 | 2440252.32 | 139147166.4 | 288.48 | 16449.6
9 | B/Nagar | Din Pur Sharif | Urban | 3603 | 119 | 35.7 | 128627.1 | 21 | 104.3 | 450951.48 | 104.3 | 450951.48 | 57 | 205371 | 98 | 353094 | 140 | 0 | 60 | 3603 | 88 | 3603 | 16 | 3603 | 80 | 3603 | 275 | 0 | 784949.58 | 48628610.1 | 217.86 | 13496.7
10 | B/Nagar | Malikpura | Urban | 8372 | 222 | 66.6 | 557575.2 | 23 | 178.4 | 1792277.76 | 178.4 | 1792277.76 | 70 | 586040 | 122 | 1021384 | 245 | 0 | 60 | 8372 | 88 | 8372 | 16 | 8372 | 80 | 8372 | 275 | 0 | 2935892.96 | 170492431.2 | 350.68 | 20364.6
11 | B/Nagar | City MCD | Urban | 9254 | 316 | 94.8 | 877279.2 | 26 | 247.2 | 2745106.56 | 247.2 | 2745106.56 | 45 | 416430 | 103 | 953162 | 342 | 0 | 60 | 9254 | 88 | 9254 | 16 | 9254 | 80 | 9254 | 275 | 0 | 4038815.76 | 224527951.2 | 436.44 | 24262.8
12 | B/Nagar | Railway Road | Urban | 43374 | 317 | 95.1 | 4124867.4 | 16 | 237.9 | 12382409.52 | 237.9 | 12382409.52 | 32 | 1387968 | 150 | 6506100 | 333 | 0 | 60 | 43374 | 88 | 43374 | 16 | 43374 | 80 | 43374 | 275 | 0 | 17895244.92 | 1145685173.4 | 412.58 | 26414.1
13 | B/Nagar | Farooq Shaheed | Urban | 4676 | 371 | 111.3 | 520438.8 | 14 | 273.7 | 1535785.44 | 273.7 | 1535785.44 | 20 | 93520 | 69 | 322644 | 385 | 0 | 60 | 4676 | 88 | 4676 | 16 | 4676 | 80 | 4676 | 275 | 0 | 2149744.24 | 113067082.8 | 459.74 | 24180.3
14 | B/Nagar | City (MSG) | Urban | 8995 | 555 | 166.5 | 1497667.5 | 40 | 428.5 | 4625229 | 428.5 | 4625229 | 33 | 296835 | 48 | 431760 | 595 | 0 | 60 | 8995 | 88 | 8995 | 16 | 8995 | 80 | 8995 | 275 | 0 | 6419731.5 | 307912342.5 | 713.7 | 34231.5
15 | B/Nagar | M/Gunj | Urban | 9330 | 373 | 111.9 | 1044027 | 30 | 291.1 | 3259155.6 | 291.1 | 3259155.6 | 7 | 65310 | 46 | 429180 | 403 | 0 | 60 | 9330 | 88 | 9330 | 16 | 0 | 80 | 9330 | 275 | 0 | 4368492.6 | 224432217 | 468.22 | 24054.9
16 | B/Nagar | Al-Mushtaq | Urban | 7078 | 378 | 113.4 | 802645.2 | 25 | 289.6 | 2459746.56 | 289.6 | 2459746.56 | 20 | 141560 | 75 | 530850 | 403 | 0 | 60 | 7078 | 88 | 7078 | 16 | 7078 | 80 | 7078 | 275 | 0 | 3403951.76 | 181843729.2 | 480.92 | 25691.4
17 | Haroonabad | CITY-I HND | Urban | 5722 | 213 | 63.9 | 365635.8 | 34 | 183.1 | 1257237.84 | 183.1 | 1257237.84 | 82 | 469204 | 127 | 726694 | 247 | 0 | 60 | 5722 | 88 | 5722 | 16 | 5722 | 80 | 5722 | 275 | 0 | 2092077.64 | 120132817.8 | 365.62 | 20994.9
18 | Haroonabad | BUNGALOW ROAD | Urban | 8851 | 280 | 84 | 743484 | 43 | 239 | 2538466.8 | 239 | 2538466.8 | 103 | 911653 | 189 | 1672839 | 322 | 1 | 60 | 8851 | 88 | 8851 | 16 | 8851 | 80 | 8851 | 275 | 0 | 4193603.8 | 254908800 | 473.8 | 28800
19 | Haroonabad | CANAL CITY | Urban | 6170 | 255 | 76.5 | 472005 | 33 | 211.5 | 1565946 | 211.5 | 1565946 | 103 | 635510 | 175 | 1079750 | 288 | 0 | 60 | 6170 | 88 | 6170 | 16 | 6170 | 80 | 6170 | 275 | 0 | 2673461 | 160157775 | 433.3 | 25957.5
20 | Haroonabad | MUSLIM CITY | Urban | 5011 | 249 | 74.7 | 374321.7 | 28 | 202.3 | 1216470.36 | 202.3 | 1216470.36 | 88 | 440968 | 143 | 716573 | 277 | 0 | 60 | 5011 | 88 | 5011 | 16 | 5011 | 80 | 5011 | 275 | 0 | 2031760.06 | 117105566.7 | 405.46 | 23369.7
21 | Haroonabad | CITY-II HND | Urban | 9175 | 515 | 154.5 | 1417537.5 | 39 | 399.5 | 4398495 | 399.5 | 4398495 | 101 | 926675 | 134 | 1229450 | 554 | 0 | 60 | 9175 | 88 | 9175 | 16 | 9175 | 80 | 9175 | 275 | 0 | 6742707.5 | 341929312.5 | 734.9 | 37267.5
22 | Haroonabad | CITY FORTABBAS | Urban | 7929 | 17 | 5.1 | 40437.9 | 2 | 13.9 | 132255.72 | 13.9 | 132255.72 | 9 | 71361 | 135 | 1070415 | 19 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 7929 | 275 | 0 | 244054.62 | 72281556.9 | 30.78 | 9116.1
23 | Haroonabad | FORT | Urban | 5124 | 26 | 7.8 | 39967.2 | 2 | 20.2 | 124205.76 | 20.2 | 124205.76 | 11 | 56364 | 88 | 450912 | 28 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 5124 | 275 | 0 | 220536.96 | 34626967.2 | 43.04 | 6757.8
24 | CHISHTIAN | COLLEGE | Urban | 12611 | 435 | 130.5 | 1645735.5 | 20 | 324.5 | 4910723.4 | 324.5 | 4910723.4 | 44 | 554884 | 41 | 517051 | 455 | 0 | 60 | 12611 | 88 | 12611 | 16 | 12611 | 80 | 12611 | 275 | 0 | 7111342.9 | 330603670.5 | 563.9 | 26215.5
25 | CHISHTIAN | CITY-I | Urban | 2681 | 82 | 24.6 | 65952.6 | 9 | 66.4 | 213622.08 | 66.4 | 213622.08 | 34 | 91154 | 69 | 184989 | 91 | 0 | 60 | 2681 | 88 | 0 | 16 | 2681 | 80 | 2681 | 275 | 0 | 370728.68 | 24114522.6 | 138.28 | 8994.6
26 | CHISHTIAN | Satellite Town | Urban | 8300 | 81 | 24.3 | 201690 | 11 | 67.7 | 674292 | 67.7 | 674292 | 41 | 340300 | 71 | 589300 | 92 | 0 | 60 | 8300 | 88 | 0 | 16 | 8300 | 80 | 8300 | 275 | 0 | 1216282 | 76420590 | 146.54 | 9207.3
27 | CHISHTIAN | Eid Gah Road | Urban | 2847 | 99 | 29.7 | 84555.9 | 3 | 72.3 | 247005.72 | 72.3 | 247005.72 | 28 | 79716 | 21 | 59787 | 102 | 0 | 60 | 2847 | 88 | 0 | 16 | 2847 | 80 | 2847 | 275 | 0 | 411277.62 | 18661230.9 | 144.46 | 6554.7
28 | CHISHTIAN | MADRASSA | Urban | 2053 | 16 | 4.8 | 9854.4 | 1 | 12.2 | 30055.92 | 12.2 | 30055.92 | 13 | 26689 | 78 | 160134 | 17 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 2053 | 275 | 0 | 66599.32 | 11440958.4 | 32.44 | 5572.8
29 | CHISHTIAN | MAIN BAZAR | Urban | 3233 | 50 | 15 | 48495 | 8 | 43 | 166822.8 | 43 | 166822.8 | 40 | 129320 | 68 | 219844 | 58 | 0 | 60 | 3233 | 88 | 0 | 16 | 3233 | 80 | 3233 | 275 | 0 | 344637.8 | 23345493 | 106.6 | 7221
30 | CHISHTIAN | CITYY-II | Urban | 5760 | 199 | 59.7 | 343872 | 13 | 152.3 | 1052697.6 | 152.3 | 1052697.6 | 44 | 253440 | 62 | 357120 | 212 | 0 | 60 | 5760 | 88 | 5760 | 16 | 5760 | 80 | 5760 | 275 | 0 | 1650009.6 | 85620672 | 286.46 | 14864.7
31 | CHISHTIAN | GHAFFARI | Urban | 4443 | 92 | 27.6 | 122626.8 | 5 | 69.4 | 370013.04 | 69.4 | 370013.04 | 43 | 191049 | 45 | 199935 | 97 | 0 | 60 | 4443 | 88 | 0 | 16 | 4443 | 80 | 4443 | 275 | 0 | 683688.84 | 34564762.8 | 153.88 | 7779.6
32 | CHISHTIAN | BAKHSHAN KHAN CITY-I | Urban | 2856 | 34 | 10.2 | 29131.2 | 3 | 26.8 | 91848.96 | 26.8 | 91848.96 | 23 | 65688 | 22 | 62832 | 37 | 0 | 60 | 0 | 88 | 0 | 16 | 2856 | 80 | 2856 | 275 | 0 | 186668.16 | 9368251.2 | 65.36 | 3280.2
33 | CHISHTIAN | BAKHSHAN KHAN CITY-II | Urban | 1730 | 29 | 8.7 | 15051 | 2 | 22.3 | 46294.8 | 22.3 | 46294.8 | 18 | 31140 | 110 | 190300 | 31 | 0 | 60 | 0 | 88 | 0 | 16 | 1730 | 80 | 1730 | 275 | 0 | 92485.8 | 14240841 | 53.46 | 8231.7
34 | CHISHTIAN | PARK | Urban | 5962 | 74 | 22.2 | 132356.4 | 11 | 62.8 | 449296.32 | 62.8 | 449296.32 | 76 | 453112 | 67 | 399454 | 85 | 0 | 60 | 5962 | 88 | 0 | 16 | 5962 | 80 | 5962 | 275 | 0 | 1034764.72 | 51322088.4 | 173.56 | 8608.2
35 | CHISHTIAN | GHULSHAN | Urban | 3052 | 39 | 11.7 | 35708.4 | 13 | 40.3 | 147594.72 | 40.3 | 147594.72 | 47 | 143444 | 72 | 219744 | 52 | 0 | 60 | 3052 | 88 | 0 | 16 | 3052 | 80 | 3052 | 275 | 0 | 326747.12 | 22147448.4 | 107.06 | 7256.7
36 | CHISHTIAN | CITY DHARAN WALA | Urban | 10099 | 210 | 63 | 636237 | 15 | 162 | 1963245.6 | 162 | 1963245.6 | 98 | 989702 | 138 | 1393662 | 225 | 0 | 60 | 10099 | 88 | 10099 | 16 | 10099 | 80 | 10099 | 275 | 0 | 3589184.6 | 203323167 | 355.4 | 20133
|  | TOTAL |  | 215983 | 5815 | 1744.5 | 16461600.3 | 526 | 4596.5 | 51269909.64 | 4596.5 | 51269909.64 | 1501 | 10974066 | 0 | 25715857 | 6340 | 1 | 60 | 196099 | 88 | 164549 | 16 | 191310 | 80 | 215983 | 275 | 0 | 78705575.94 | 4668530799.3 | 364.4063 | 21615.2697

## 400-220 (Urban) Khanewal
Statement of 400/220 V MEPCO Consumers For 2020-21
Khanewal Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | Khanewal | City-I (KWL) | Urban | 5871 | 132 | 39.6 | 232491.6 | 15 | 107.4 | 756654.48 | 107.4 | 756654.48 | 197 | 1156587 | 209.45 | 1229680.95 | 147 | 0 | 60 | 5871 | 88 | 5871 | 16 | 5871 | 80 | 5871 | 275 | 0 | 2145733.08 | 119877600.6 | 365.48 | 20418.6
2 | Khanewal | City II (KWL) | Urban | 9481 | 119 | 35.7 | 338471.7 | 14 | 97.3 | 1107001.56 | 97.3 | 1107001.56 | 77 | 730037 | 96.3 | 913020.3 | 133 | 0 | 60 | 9481 | 88 | 9481 | 16 | 9481 | 80 | 9481 | 275 | 0 | 2175510.26 | 122216726.7 | 229.46 | 12890.7
3 | Khanewal | City-III (KWL) | Urban | 4882 | 130 | 39 | 190398 | 12 | 103 | 603415.2 | 103 | 603415.2 | 7 | 34174 | 28.4 | 138648.8 | 142 | 0 | 60 | 4882 | 88 | 4882 | 16 | 0 | 80 | 0 | 275 | 0 | 827987.2 | 45095034 | 169.6 | 9237
4 | Khanewal | City-IV (KWL) | Urban | 3439 | 118 | 35.4 | 121740.6 | 13 | 95.6 | 394522.08 | 95.6 | 394522.08 | 5 | 17195 | 24.35 | 83739.65 | 131 | 0 | 60 | 3439 | 88 | 3439 | 16 | 0 | 80 | 0 | 275 | 0 | 533457.68 | 29060925.6 | 155.12 | 8450.4
5 | Khanewal | City-V (KWL) | Urban | 3329 | 50 | 15 | 49935 | 9 | 44 | 175771.2 | 44 | 175771.2 | 6 | 19974 | 26.5 | 88218.5 | 59 | 0 | 60 | 3329 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 245680.2 | 15989187 | 73.8 | 4803
6 | Khanewal | Cold Storage | Urban | 4790 | 219 | 65.7 | 314703 | 16 | 169.3 | 973136.4 | 169.3 | 973136.4 | 9 | 43110 | 37.15 | 177948.5 | 235 | 0 | 60 | 4790 | 88 | 4790 | 16 | 0 | 80 | 0 | 275 | 0 | 1330949.4 | 70009203 | 277.86 | 14615.7
7 | Khanewal | Kot Madina | Urban | 3720 | 88 | 26.4 | 98208 | 20 | 81.6 | 364262.4 | 81.6 | 364262.4 | 6 | 22320 | 26.25 | 97650 | 108 | 0 | 60 | 3720 | 88 | 3720 | 16 | 0 | 80 | 0 | 275 | 0 | 484790.4 | 28009368 | 130.32 | 7529.4
8 | Khanewal | Ibrahim City | Urban | 26 | 21 | 6.3 | 163.8 | 1 | 15.7 | 489.84 | 15.7 | 489.84 | 7 | 182 | 31.4 | 816.4 | 22 | 0 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 835.64 | 78865.8 | 32.14 | 3033.3
9 | Khanewal | Colony | Urban | 9456 | 140 | 42 | 397152 | 20 | 118 | 1338969.6 | 118 | 1338969.6 | 7 | 66192 | 29.15 | 275642.4 | 160 | 0 | 60 | 9456 | 88 | 9456 | 16 | 0 | 80 | 0 | 275 | 0 | 1802313.6 | 98068176 | 190.6 | 10371
10 | Khanewal | Colony-II | Urban | 8521 | 139 | 41.7 | 355325.7 | 13 | 110.3 | 1127839.56 | 110.3 | 1127839.56 | 251 | 2138771 | 269.25 | 2294279.25 | 152 | 0 | 60 | 8521 | 88 | 8521 | 16 | 8521 | 80 | 8521 | 275 | 0 | 3621936.26 | 206393105.7 | 425.06 | 24221.7
11 | Khanewal | City-I (JHN) | Urban | 8777 | 335 | 100.5 | 882088.5 | 22 | 256.5 | 2701560.6 | 256.5 | 2701560.6 | 125 | 1097125 | 4.3972 | 38594.4194 | 357 | 0 | 60 | 8777 | 88 | 8777 | 16 | 8777 | 80 | 0 | 275 | 0 | 4680774.1 | 167055566.6667 | 533.3 | 19033.3333
12 | Kabirwala | CITY KABIRWALA | Urban | 7505 | 272 | 81.6 | 612408 | 10 | 200.4 | 1804802.4 | 200.4 | 1804802.4 | 49 | 367745 | 271.3 | 2036106.5 | 274 | 8 | 60 | 7505 | 88 | 7505 | 16 | 7505 | 80 | 7505 | 275 | 0 | 2784955.4 | 232291758 | 371.08 | 30951.6
13 | Kabirwala | PIR KABIR | Urban | 8561 | 190 | 57 | 487977 | 20 | 153 | 1571799.6 | 153 | 1571799.6 | 59 | 505099 | 798.15 | 6832962.15 | 209 | 1 | 60 | 8561 | 88 | 8561 | 16 | 8561 | 80 | 8561 | 275 | 0 | 2564875.6 | 505749636 | 299.6 | 59076
14 | Kabirwala | CITY-2 | Urban | 4131 | 66 | 19.8 | 81793.8 | 8 | 54.2 | 268680.24 | 54.2 | 268680.24 | 22 | 90882 | 54.31 | 224354.61 | 74 | 0 | 60 | 4131 | 88 | 0 | 16 | 4131 | 80 | 0 | 275 | 0 | 441356.04 | 29827472.4 | 106.84 | 7220.4
15 | Kabirwala | CITY M/PUR | Urban | 5530 | 231 | 69.3 | 383229 | 43 | 204.7 | 1358389.2 | 204.7 | 1358389.2 | 15 | 82950 | 30 | 165900 | 274 | 0 | 60 | 5530 | 88 | 5530 | 16 | 5530 | 80 | 0 | 275 | 0 | 1824568.2 | 92607039 | 329.94 | 16746.3
16 | Mian Channu | City-I | Urban | 5461 | 82 | 24.6 | 134340.6 | 19 | 76.4 | 500664.48 | 76.4 | 500664.48 | 58 | 316738 | 94.15 | 514153.15 | 101 | 0 | 60 | 5461 | 88 | 5461 | 16 | 5461 | 80 | 5461 | 275 | 0 | 951743.08 | 61292079.6 | 174.28 | 11223.6
17 | Mian Channu | City-3 | Urban | 7486 | 42 | 12.6 | 94323.6 | 7 | 36.4 | 326988.48 | 36.4 | 326988.48 | 43 | 321898 | 88.5 | 662511 | 49 | 0 | 60 | 0 | 88 | 0 | 16 | 7486 | 80 | 7486 | 275 | 0 | 743210.08 | 59652939.6 | 99.28 | 7968.6
18 | Mian Channu | City-5 | Urban | 6157 | 40 | 12 | 73884 | 10 | 38 | 280759.2 | 38 | 280759.2 | 93 | 572601 | 127 | 781939 | 49 | 1 | 60 | 0 | 88 | 0 | 16 | 6157 | 80 | 6157 | 275 | 0 | 927244.2 | 63983544 | 150.6 | 10392
19 | Mian Channu | City-2 | Urban | 6724 | 62 | 18.6 | 125066.4 | 14 | 57.4 | 463149.12 | 57.4 | 463149.12 | 57 | 383268 | 82.3 | 553385.2 | 74 | 2 | 60 | 6724 | 88 | 0 | 16 | 6724 | 80 | 6724 | 275 | 0 | 971483.52 | 61367258.4 | 144.48 | 9126.6
20 | Mian Channu | City-4 | Urban | 7300 | 143 | 42.9 | 313170 | 31 | 131.1 | 1148436 | 131.1 | 1148436 | 109 | 795700 | 313.1 | 2285630 | 171 | 3 | 60 | 7300 | 88 | 7300 | 16 | 7300 | 80 | 7300 | 275 | 0 | 2257306 | 206983470 | 309.22 | 28353.9
21 | Mian Channu | Bura Road | Urban | 6989 | 43 | 12.9 | 90158.1 | 9 | 39.1 | 327923.88 | 39.1 | 327923.88 | 75 | 524175 | 113.25 | 791504.25 | 48 | 4 | 60 | 0 | 88 | 0 | 16 | 6989 | 80 | 6989 | 275 | 0 | 942256.98 | 67436162.1 | 134.82 | 9648.9
22 | Mian Channu | Latif Bagh H/Scheme | Urban | 105 | 6 | 1.8 | 189 | 1 | 5.2 | 655.2 | 5.2 | 655.2 | 10 | 1050 | 33.25 | 3491.25 | 6 | 1 | 60 | 0 | 88 | 0 | 16 | 0 | 80 | 0 | 275 | 0 | 1894.2 | 249354 | 18.04 | 2374.8
23 | Mian Channu | City A/Hakim | Urban | 6851 | 536 | 160.8 | 1101640.8 | 17 | 392.2 | 3224354.64 | 392.2 | 3224354.64 | 22 | 150722 | 64.42 | 441341.42 | 553 | 6 | 60 | 6851 | 88 | 6851 | 16 | 6851 | 80 | 0 | 275 | 0 | 4476717.44 | 223246686 | 653.44 | 32586
24 | Mian Channu | Sidhnai | Urban | 10962 | 305 | 91.5 | 1003023 | 11 | 224.5 | 2953162.8 | 224.5 | 2953162.8 | 34 | 372708 | 75.17 | 824013.54 | 316 | 7 | 60 | 10962 | 88 | 10962 | 16 | 10962 | 80 | 0 | 275 | 0 | 4328893.8 | 229639649.4 | 394.9 | 20948.7
25 | Mian Channu | Tulamba City-2 | Urban | 6854 | 268 | 80.4 | 551061.6 | 7 | 194.6 | 1600546.08 | 194.6 | 1600546.08 | 6 | 41124 | 26.45 | 181288.3 | 275 | 8 | 60 | 6854 | 88 | 6854 | 16 | 0 | 80 | 0 | 275 | 0 | 2192731.68 | 108563247.6 | 319.92 | 15839.4
|  | TOTAL |  | 100966 | 3546 | 712.2 | 4774749.9 | 219 | 1923.8 | 15374947.32 | 1923.8 | 15374947.32 | 928 | 7010979 | 2119.0072 | 15774226.5794 | 4119 | 41 | 60 | 93454 | 88 | 85994 | 16 | 71324 | 80 | 52886 | 275 | 0 | 27160676.22 | 1883274683.6667 | 269.0081 | 18652.5631

## 400-220 (Rural) Multan
Statement of 400/220 V MEPCO Consumers For 2020-21
Multan Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | Cantt | LABAR | Rural | 5237 | 221 | 66.3 | 347213.1 | 55 | 209.7 | 1317838.68 | 419.4 | 2635677.36 | 21 | 109977 | 99 | 518463 | 276 | 0 | 80 | 5237 | 175 | 5237 | 16 | 5237 | 96 | 5237 | 300 | 0 | 1775028.78 | 190290060.9 | 338.94 | 36335.7
2 | Cantt | BAHAUDDIN ZAKARIYA | Rural | 7532 | 384 | 115.2 | 867686.4 | 20 | 288.8 | 2610289.92 | 577.6 | 5220579.84 | 15 | 112980 | 67 | 504644 | 404 | 0 | 80 | 7532 | 175 | 7532 | 16 | 0 | 96 | 0 | 300 | 0 | 3590956.32 | 346116489.6 | 476.76 | 45952.8
3 | Mumtazabad | L.A.R OLD | Rural | 2307 | 230 | 69 | 159183 | 118 | 279 | 772383.6 | 558 | 1544767.2 | 8 | 18456 | 31.5 | 72670.5 | 348 | 0 | 80 | 2307 | 175 | 2307 | 16 | 0 | 96 | 0 | 300 | 0 | 950022.6 | 97523811 | 411.8 | 42273
4 | Mumtazabad | A&B/GHEEMILL | Rural | 2228 | 178 | 53.4 | 118975.2 | 100 | 224.6 | 600490.56 | 449.2 | 1200981.12 | 12 | 26736 | 0 | 0 | 278 | 0 | 80 | 2228 | 175 | 2228 | 16 | 0 | 96 | 0 | 300 | 0 | 746201.76 | 72415792.8 | 334.92 | 32502.6
5 | Mumtazabad | NEW LAR | Rural | 3929 | 279 | 83.7 | 328857.3 | 203 | 398.3 | 1877904.84 | 796.6 | 3755809.68 | 108 | 424332 | 46.45 | 182502.05 | 482 | 0 | 80 | 3929 | 175 | 3929 | 16 | 3929 | 96 | 0 | 300 | 0 | 2631094.14 | 237285275.7 | 669.66 | 60393.3
6 | Mumtazabad | BWP ROAD | Rural | 4759 | 80 | 24 | 114216 | 121 | 177 | 1010811.6 | 354 | 2021623.2 | 20 | 95180 | 100.13 | 476518.67 | 201 | 0 | 80 | 4759 | 175 | 4759 | 16 | 4759 | 96 | 4759 | 300 | 0 | 1220207.6 | 150231160.2 | 256.4 | 31567.8
7 | Mumtazabad | PIR ISMAIL | Rural | 2992 | 260 | 78 | 233376 | 168 | 350 | 1256640 | 700 | 2513280 | 18 | 53856 | 76.53 | 228977.76 | 428 | 0 | 80 | 2992 | 175 | 2992 | 16 | 2992 | 96 | 0 | 300 | 0 | 1543872 | 165235593.6 | 516 | 55225.8
8 | Mumtazabad | VEHARI ROAD | Rural | 3805 | 387 | 116.1 | 441760.5 | 156 | 426.9 | 1949225.4 | 853.8 | 3898450.8 | 9 | 34245 | 36.28 | 138045.4 | 543 | 0 | 80 | 3805 | 175 | 3805 | 16 | 0 | 96 | 0 | 300 | 0 | 2425230.9 | 243515053.5 | 637.38 | 63998.7
9 | Mumtazabad | DUNYA PUR ROAD | Rural | 6223 | 277 | 83.1 | 517131.3 | 220 | 413.9 | 3090839.64 | 827.8 | 6181679.28 | 9 | 56007 | 24 | 149352 | 497 | 0 | 80 | 6223 | 175 | 6223 | 16 | 0 | 96 | 0 | 300 | 0 | 3663977.94 | 381413270.7 | 588.78 | 61290.9
10 | Mumtazabad | QUAID-E-AZAM | Rural | 4974 | 226 | 67.8 | 337237.2 | 73 | 231.2 | 1379986.56 | 462.4 | 2759973.12 | 12 | 59688 | 42.43 | 211046.82 | 299 | 0 | 80 | 4974 | 175 | 4974 | 16 | 0 | 96 | 0 | 300 | 0 | 1776911.76 | 179272908 | 357.24 | 36042
11 | Mumtazabad | SAHU | Rural | 4186 | 333 | 99.9 | 418181.4 | 95 | 328.1 | 1648111.92 | 656.2 | 3296223.84 | 8 | 33488 | 32.25 | 134998.5 | 428 | 0 | 80 | 4186 | 175 | 4186 | 16 | 0 | 96 | 0 | 300 | 0 | 2099781.32 | 207127884.6 | 501.62 | 49481.1
12 | Mumtazabad | PEER FAKAR ALI | Rural | 4321 | 273 | 81.9 | 353889.9 | 129 | 320.1 | 1659782.52 | 640.2 | 3319565.04 | 8 | 34568 | 29.45 | 127253.45 | 402 | 0 | 80 | 4321 | 175 | 4321 | 16 | 0 | 96 | 0 | 300 | 0 | 2048240.42 | 207870779.1 | 474.02 | 48107.1
13 | Mumtazabad | KHAN PUR MARAL | Rural | 4032 | 322 | 96.6 | 389491.2 | 190 | 415.4 | 2009871.36 | 830.8 | 4019742.72 | 8 | 32256 | 31.05 | 125193.6 | 512 | 0 | 80 | 4032 | 175 | 4032 | 16 | 0 | 96 | 0 | 300 | 0 | 2431618.56 | 249864652.8 | 603.08 | 61970.4
14 | Mumtazabad | BUDHLA SANT | Rural | 6796 | 293 | 87.9 | 597368.4 | 109 | 314.1 | 2561548.32 | 628.2 | 5123096.64 | 18 | 122328 | 80.25 | 545379 | 402 | 0 | 80 | 6796 | 175 | 6796 | 16 | 6796 | 96 | 0 | 300 | 0 | 3281244.72 | 341900643.6 | 482.82 | 50309.1
15 | Mumtazabad | BORIAN WALA | Rural | 2527 | 408 | 122.4 | 309304.8 | 113 | 398.6 | 1208714.64 | 797.2 | 2417429.28 | 214 | 540778 | 225 | 568575 | 521 | 0 | 80 | 2527 | 175 | 2527 | 16 | 2527 | 96 | 2527 | 300 | 0 | 2058797.44 | 180088171.2 | 814.72 | 71265.6
16 | Mumtazabad | TUBEWELL | Rural | 3276 | 273 | 81.9 | 268304.4 | 75 | 266.1 | 1046092.32 | 532.2 | 2092184.64 | 84 | 275184 | 120 | 393120 | 347 | 1 | 80 | 3276 | 175 | 3276 | 16 | 3276 | 96 | 3276 | 300 | 0 | 1589580.72 | 149923191.6 | 485.22 | 45764.1
17 | Mumtazabad | CHAK 5-FAIZ | Rural | 2428 | 135 | 40.5 | 98334 | 105 | 199.5 | 581263.2 | 399 | 1162526.4 | 296 | 718688 | 314 | 762392 | 240 | 0 | 80 | 2428 | 175 | 2428 | 16 | 2428 | 96 | 2428 | 300 | 0 | 1398285.2 | 115790106 | 575.9 | 47689.5
18 | Mumtazabad | JAM PUR | Rural | 4836 | 392 | 117.6 | 568713.6 | 117 | 391.4 | 2271372.48 | 782.8 | 4542744.96 | 9 | 43524 | 18 | 87048 | 509 | 0 | 80 | 4836 | 175 | 4836 | 16 | 0 | 96 | 0 | 300 | 0 | 2883610.08 | 279493718.4 | 596.28 | 57794.4
19 | Mumtazabad | TUBEWELL-2 | Rural | 4531 | 113 | 33.9 | 153600.9 | 39 | 118.1 | 642133.32 | 236.2 | 1284266.64 | 232 | 1051192 | 266.2 | 1206152.2 | 151 | 1 | 80 | 4531 | 175 | 4531 | 16 | 4531 | 96 | 4531 | 300 | 0 | 1846926.22 | 149885933.1 | 407.62 | 33080.1
20 | Mumtazabad | MUHAMMAD PUR | Rural | 4456 | 227 | 68.1 | 303453.6 | 69 | 227.9 | 1218626.88 | 455.8 | 2437253.76 | 11 | 49016 | 15.3 | 68176.8 | 295 | 1 | 80 | 4456 | 175 | 4456 | 16 | 0 | 96 | 0 | 300 | 0 | 1571096.48 | 151236194.4 | 352.58 | 33939.9
21 | Mumtazabad | TAHIR ABAD | Rural | 4589 | 324 | 97.2 | 446050.8 | 81 | 307.8 | 1694993.04 | 615.6 | 3389986.08 | 10 | 45890 | 16 | 73424 | 405 | 0 | 80 | 4589 | 175 | 4589 | 16 | 0 | 96 | 0 | 300 | 0 | 2186933.84 | 209142757.2 | 476.56 | 45574.8
22 | Mumtazabad | PIR BUKHSH MARAL | Rural | 5749 | 288 | 86.4 | 496713.6 | 76 | 277.6 | 1915106.88 | 555.2 | 3830213.76 | 9 | 51741 | 38 | 218462 | 364 | 0 | 80 | 5749 | 175 | 5749 | 16 | 0 | 96 | 0 | 300 | 0 | 2463561.48 | 244410686.4 | 428.52 | 42513.6
23 | Mumtazabad | LAR CITY | Rural | 4595 | 151 | 45.3 | 208153.5 | 72 | 177.7 | 979837.8 | 355.4 | 1959675.6 | 9 | 41355 | 6 | 27570 | 223 | 0 | 80 | 4595 | 175 | 4595 | 16 | 0 | 96 | 0 | 300 | 0 | 1229346.3 | 119859196.5 | 267.54 | 26084.7
24 | Mumtazabad | ISLAM PUR | Rural | 5557 | 643 | 192.9 | 1071945.3 | 83 | 533.1 | 3554924.04 | 1066.2 | 7109848.08 | 9 | 50013 | 21 | 116697 | 726 | 0 | 80 | 5557 | 175 | 5557 | 16 | 0 | 96 | 0 | 300 | 0 | 4676882.34 | 436808540.7 | 841.62 | 78605.1
25 | Mumtazabad | TUBEWELL-3 | Rural | 2381 | 143 | 42.9 | 102144.9 | 56 | 156.1 | 446008.92 | 312.2 | 892017.84 | 10 | 23810 | 44.35 | 105597.35 | 199 | 0 | 80 | 2381 | 175 | 2381 | 16 | 0 | 96 | 0 | 300 | 0 | 571963.82 | 60163346.1 | 240.22 | 25268.1
26 | Mumtazabad | JALAL SHAH | Rural | 2795 | 305 | 91.5 | 255742.5 | 61 | 274.5 | 920673 | 549 | 1841346 | 60 | 167700 | 85.2 | 238134 | 366 | 0 | 80 | 2795 | 175 | 2795 | 16 | 2795 | 96 | 0 | 300 | 0 | 1344115.5 | 125536027.5 | 480.9 | 44914.5
27 | City | PEER HASAN SAWALI | Rural | 5502 | 129 | 38.7 | 212927.4 | 81 | 171.3 | 1130991.12 | 342.6 | 2261982.24 | 27 | 148554 | 66.15 | 363957.3 | 210 | 0 | 80 | 5502 | 175 | 5502 | 16 | 5502 | 96 | 0 | 300 | 0 | 1492472.52 | 158195154.6 | 271.26 | 28752.3
28 | City | RANGEEL PUR | Rural | 2686 | 69 | 20.7 | 55600.2 | 37 | 85.3 | 274938.96 | 170.6 | 549877.92 | 28 | 75208 | 66.15 | 177678.9 | 106 | 0 | 80 | 2686 | 175 | 2686 | 16 | 2686 | 96 | 0 | 300 | 0 | 405747.16 | 43820209.8 | 151.06 | 16314.3
29 | City | SHER SHAH | Rural | 10510 | 814 | 244.2 | 2566542 | 32 | 601.8 | 7589901.6 | 1203.6 | 15179803.2 | 35 | 367850 | 123.55 | 1298510.5 | 846 | 0 | 80 | 10510 | 175 | 10510 | 16 | 10510 | 96 | 10510 | 300 | 0 | 10524293.6 | 996398448 | 1001.36 | 94804.8
30 | City | KHOKHAR | Rural | 4812 | 427 | 128.1 | 616417.2 | 17 | 315.9 | 1824132.96 | 631.8 | 3648265.92 | 14 | 67368 | 58.45 | 281261.4 | 444 | 0 | 80 | 4812 | 175 | 4812 | 16 | 0 | 96 | 0 | 300 | 0 | 2507918.16 | 237620890.8 | 521.18 | 49380.9
31 | City | QASIM BELA | Rural | 7996 | 80 | 24 | 191904 | 27 | 83 | 796401.6 | 166 | 1592803.2 | 11 | 87956 | 20.45 | 163518.2 | 107 | 0 | 80 | 7996 | 175 | 7996 | 16 | 0 | 96 | 0 | 300 | 0 | 1076261.6 | 105954996 | 134.6 | 13251
32 | City | CHENAB | Rural | 5590 | 373 | 111.9 | 625521 | 19 | 280.1 | 1878910.8 | 560.2 | 3757821.6 | 31 | 173290 | 96.55 | 539714.5 | 392 | 0 | 80 | 5590 | 175 | 5590 | 16 | 5590 | 96 | 5590 | 300 | 0 | 2677721.8 | 259728729 | 479.02 | 46463.1
33 | City | GULSHAN IQBAL | Rural | 5296 | 75 | 22.5 | 119160 | 13 | 65.5 | 416265.6 | 131 | 832531.2 | 11 | 58256 | 14.4 | 76262.4 | 88 | 0 | 80 | 5296 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 593681.6 | 54885096 | 112.1 | 10363.5
34 | City | BASTI BALAIL | Rural | 8702 | 512 | 153.6 | 1336627.2 | 27 | 385.4 | 4024500.96 | 770.8 | 8049001.92 | 21 | 182742 | 67 | 583034 | 539 | 0 | 80 | 8702 | 175 | 8702 | 16 | 8702 | 96 | 0 | 300 | 0 | 5543870.16 | 521932036.8 | 637.08 | 59978.4
35 | City | KHAIR PUR BHUTTA | Rural | 2257 | 194 | 58.2 | 131357.4 | 15 | 150.8 | 408426.72 | 301.6 | 816853.44 | 24 | 54168 | 84.55 | 190829.35 | 209 | 0 | 80 | 2257 | 175 | 2257 | 16 | 2257 | 96 | 0 | 300 | 0 | 593952.12 | 60855039.6 | 263.16 | 26962.8
36 | Shujabad | NAWAB LIAQAT ALI | Rural | 4757 | 508 | 152.4 | 724966.8 | 81 | 436.6 | 2492287.44 | 873.2 | 4984574.88 | 18 | 85626 | 47 | 223579 | 589 | 0 | 80 | 4757 | 175 | 4757 | 16 | 4757 | 96 | 0 | 300 | 0 | 3302880.24 | 314664133.2 | 694.32 | 66147.6
37 | Shujabad | AL-FAREED | Rural | 8361 | 442 | 132.6 | 1108668.6 | 71 | 380.4 | 3816629.28 | 760.8 | 7633258.56 | 122 | 1020042 | 54 | 451494 | 513 | 0 | 80 | 8361 | 175 | 8361 | 16 | 8361 | 96 | 0 | 300 | 0 | 5945339.88 | 488411159.4 | 711.08 | 58415.4
38 | Shujabad | MACCAY WALA | Rural | 6330 | 218 | 65.4 | 413982 | 113 | 265.6 | 2017497.6 | 531.2 | 4034995.2 | 232 | 1468560 | 362.4 | 2293992 | 331 | 0 | 80 | 6330 | 175 | 6330 | 16 | 6330 | 96 | 6330 | 300 | 0 | 3900039.6 | 380981178 | 616.12 | 60186.6
39 | Shujabad | KOTLY NAJABAT | Rural | 7460 | 293 | 87.9 | 655734 | 50 | 255.1 | 2283655.2 | 510.2 | 4567310.4 | 239 | 1782940 | 237.15 | 1769139 | 343 | 0 | 80 | 7460 | 175 | 7460 | 16 | 7460 | 96 | 7460 | 300 | 0 | 4722329.2 | 382154166 | 633.02 | 51227.1
40 | Shujabad | BASTI MALOOK | Rural | 4907 | 561 | 168.3 | 825848.1 | 109 | 501.7 | 2954210.28 | 1003.4 | 5908420.56 | 37 | 181559 | 80 | 392560 | 670 | 0 | 80 | 4907 | 175 | 4907 | 16 | 4907 | 96 | 0 | 300 | 0 | 3961617.38 | 380536377.9 | 807.34 | 77549.7
41 | Shujabad | KHAWAJA KHUDA YAR | Rural | 6777 | 577 | 173.1 | 1173098.7 | 76 | 479.9 | 3902738.76 | 959.8 | 7805477.52 | 366 | 2480382 | 154 | 1043658 | 653 | 0 | 80 | 6777 | 175 | 6777 | 16 | 6777 | 96 | 6777 | 300 | 0 | 7556219.46 | 534467427.3 | 1114.98 | 78864.9
42 | Shujabad | IMAM SHAH | Rural | 10874 | 536 | 160.8 | 1748539.2 | 71 | 446.2 | 5822374.56 | 892.4 | 11644749.12 | 69 | 750306 | 78 | 848172 | 607 | 0 | 80 | 10874 | 175 | 10874 | 16 | 10874 | 96 | 0 | 300 | 0 | 8321219.76 | 754820884.8 | 765.24 | 69415.2
43 | Shujabad | MATTOLY | Rural | 3654 | 217 | 65.1 | 237875.4 | 7 | 158.9 | 696744.72 | 317.8 | 1393489.44 | 8 | 29232 | 1.6771 | 6128.0625 | 224 | 0 | 80 | 3654 | 175 | 3654 | 16 | 0 | 96 | 0 | 300 | 0 | 963852.12 | 84690676.35 | 263.78 | 23177.525
44 | Shujabad | T.WELL | Rural | 8293 | 415 | 124.5 | 1032478.5 | 76 | 366.5 | 3647261.4 | 733 | 7294522.8 | 73 | 605389 | 52 | 431236 | 491 | 0 | 80 | 8293 | 175 | 8293 | 16 | 8293 | 96 | 0 | 300 | 0 | 5285128.9 | 466642963.5 | 637.3 | 56269.5
45 | Shujabad | AL-KARAM | Rural | 4482 | 331 | 99.3 | 445062.6 | 65 | 296.7 | 1595771.28 | 593.4 | 3191542.56 | 25 | 112050 | 31 | 138942 | 396 | 0 | 80 | 4482 | 175 | 4482 | 16 | 4482 | 96 | 0 | 300 | 0 | 2152883.88 | 201164261.4 | 480.34 | 44882.7
46 | Shujabad | AL-FAZAL | Rural | 7620 | 529 | 158.7 | 1209294 | 54 | 424.3 | 3879799.2 | 848.6 | 7759598.4 | 87 | 662940 | 77 | 586740 | 583 | 0 | 80 | 7620 | 175 | 7620 | 16 | 7620 | 96 | 0 | 300 | 0 | 5752033.2 | 504408186 | 754.86 | 66195.3
47 | Shujabad | THATH GHALWAN | Rural | 3762 | 300 | 90 | 338580 | 6 | 216 | 975110.4 | 432 | 1950220.8 | 186 | 699732 | 8.6597 | 32577.875 | 306 | 0 | 80 | 3762 | 175 | 3762 | 16 | 3762 | 96 | 0 | 300 | 0 | 2013422.4 | 119983660.5 | 535.2 | 31893.5833
48 | Shujabad | QASBA MARAL | Rural | 6459 | 390 | 117 | 755703 | 62 | 335 | 2596518 | 670 | 5193036 | 54 | 348786 | 47 | 303573 | 452 | 0 | 80 | 6459 | 175 | 6459 | 16 | 6459 | 96 | 0 | 300 | 0 | 3701007 | 332063649 | 573 | 51411
49 | Shujabad | INDUSTRIAL | Rural | 6544 | 462 | 138.6 | 906998.4 | 68 | 391.4 | 3073585.92 | 782.8 | 6147171.84 | 37 | 242128 | 48 | 314112 | 530 | 0 | 80 | 6544 | 175 | 6544 | 16 | 6544 | 96 | 0 | 300 | 0 | 4222712.32 | 390398025.6 | 645.28 | 59657.4
50 | Shujabad | SABRA | Rural | 5745 | 409 | 122.7 | 704911.5 | 94 | 380.3 | 2621788.2 | 760.6 | 5243576.4 | 128 | 735360 | 191.23 | 1098616.35 | 503 | 0 | 80 | 5745 | 175 | 5745 | 16 | 5745 | 96 | 5745 | 300 | 0 | 4062059.7 | 382646299.5 | 707.06 | 66605.1
51 | Shujabad | KHANBELA | Rural | 8945 | 578 | 173.4 | 1551063 | 140 | 544.6 | 5845736.4 | 1089.2 | 11691472.8 | 10 | 89450 | 35.5 | 317547.5 | 718 | 0 | 80 | 8945 | 175 | 8945 | 16 | 0 | 96 | 0 | 300 | 0 | 7486249.4 | 725194407 | 836.92 | 81072.6
52 | Shujabad | BAHADARPUR | Rural | 3277 | 847 | 254.1 | 832685.7 | 121 | 713.9 | 2807340.36 | 1427.8 | 5614680.72 | 66 | 216282 | 207.19 | 678961.63 | 968 | 0 | 80 | 3277 | 175 | 3277 | 16 | 3277 | 96 | 3277 | 300 | 0 | 3856308.06 | 380116598.1 | 1176.78 | 115995.3
53 | Shujabad | JAFFAR ABAD | Rural | 5986 | 463 | 138.9 | 831455.4 | 108 | 432.1 | 3103860.72 | 864.2 | 6207721.44 | 67 | 401062 | 90.1 | 539338.6 | 571 | 0 | 80 | 5986 | 175 | 5986 | 16 | 5986 | 96 | 0 | 300 | 0 | 4336378.12 | 407317968.6 | 724.42 | 68045.1
54 | Shujabad | KOTLA | Rural | 7958 | 1037 | 311.1 | 2475733.8 | 144 | 869.9 | 8307197.04 | 1739.8 | 16614394.08 | 13 | 103454 | 51.27 | 408006.66 | 1181 | 0 | 80 | 7958 | 175 | 7958 | 16 | 0 | 96 | 0 | 300 | 7958 | 10886384.84 | 1028771245.8 | 1367.98 | 129275.1
55 | Shujabad | ALIPUR | Rural | 3858 | 241 | 72.3 | 278933.4 | 97 | 265.7 | 1230084.72 | 531.4 | 2460169.44 | 9 | 34722 | 34 | 131172 | 338 | 0 | 80 | 3858 | 175 | 3858 | 16 | 0 | 96 | 0 | 300 | 0 | 1543740.12 | 156317286.6 | 400.14 | 40517.7
56 | Shujabad | QADIR PUR | Rural | 3050 | 388 | 116.4 | 355020 | 101 | 372.6 | 1363716 | 745.2 | 2727432 | 10 | 30500 | 33.4 | 101870 | 489 | 0 | 80 | 3050 | 175 | 3050 | 16 | 0 | 96 | 0 | 300 | 0 | 1749236 | 170823180 | 573.52 | 56007.6
57 | Shujabad | BEHLI SHARIF | Rural | 5212 | 496 | 148.8 | 775545.6 | 116 | 463.2 | 2897038.08 | 926.4 | 5794076.16 | 245 | 1276940 | 311.39 | 1622964.68 | 612 | 0 | 80 | 5212 | 175 | 5212 | 16 | 5212 | 96 | 5212 | 300 | 0 | 4949523.68 | 447349087.2 | 949.64 | 85830.6
58 | Shujabad | INDUSTRIAL | Rural | 5053 | 268 | 80.4 | 406261.2 | 83 | 270.6 | 1640810.16 | 541.2 | 3281620.32 | 62 | 313286 | 195.15 | 986092.95 | 351 | 0 | 80 | 5053 | 175 | 5053 | 16 | 5053 | 96 | 5053 | 300 | 0 | 2360357.36 | 257281579.8 | 467.12 | 50916.6
59 | Shujabad | GHAZI PUR | Rural | 4564 | 514 | 154.2 | 703768.8 | 131 | 490.8 | 2688013.44 | 981.6 | 5376026.88 | 10 | 45640 | 40.15 | 183244.6 | 645 | 0 | 80 | 4564 | 175 | 4564 | 16 | 0 | 96 | 0 | 300 | 0 | 3437422.24 | 335667595.2 | 753.16 | 73546.8
60 | Shujabad | JUGGO WALA | Rural | 5823 | 494 | 148.2 | 862968.6 | 17 | 362.8 | 2535101.28 | 725.6 | 5070202.56 | 372 | 2166156 | 14.1354 | 82310.5312 | 511 | 0 | 80 | 5823 | 175 | 5823 | 16 | 5823 | 96 | 0 | 300 | 0 | 5564225.88 | 311739691.275 | 955.56 | 53535.925
61 | Shujabad | PEER QATAR | Rural | 2235 | 215 | 64.5 | 144157.5 | 90 | 240.5 | 645021 | 481 | 1290042 | 406 | 907410 | 548.05 | 1224891.75 | 305 | 0 | 80 | 2235 | 175 | 2235 | 16 | 2235 | 96 | 2235 | 300 | 0 | 1696588.5 | 151328497.5 | 759.1 | 67708.5
62 | Shujabad | ZAFFAR ABAD | Rural | 6274 | 211 | 63.3 | 397144.2 | 99 | 246.7 | 1857354.96 | 493.4 | 3714709.92 | 10 | 62740 | 37.1 | 232765.4 | 310 | 0 | 80 | 6274 | 175 | 6274 | 16 | 0 | 96 | 0 | 300 | 0 | 2317239.16 | 238039951.8 | 369.34 | 37940.7
63 | Shujabad | MAKHDOOM JAHANIAN | Rural | 7900 | 492 | 147.6 | 1166040 | 98 | 442.4 | 4193952 | 884.8 | 8387904 | 62 | 489800 | 400.25 | 3161975 | 590 | 0 | 80 | 7900 | 175 | 7900 | 16 | 7900 | 96 | 7900 | 300 | 0 | 5849792 | 696490860 | 740.48 | 88163.4
64 | B.Z (Musa Pak) | DAHER | Rural | 7117 | 243 | 72.9 | 518829.3 | 173 | 343.1 | 2930211.24 | 686.2 | 5860422.48 | 45 | 320265 | 78.35 | 557616.95 | 416 | 0 | 80 | 7117 | 175 | 7117 | 16 | 7117 | 96 | 0 | 300 | 0 | 3769305.54 | 386638853.7 | 529.62 | 54326.1
65 | B.Z (Musa Pak) | S.T.M. | Rural | 2294 | 71 | 21.3 | 48862.2 | 19 | 68.7 | 189117.36 | 137.4 | 378234.72 | 13 | 29822 | 34.3 | 78684.2 | 90 | 0 | 80 | 2294 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 267801.56 | 27561721.8 | 116.74 | 12014.7
66 | B.Z (Musa Pak) | SHAKH MADINA | Rural | 3684 | 127 | 38.1 | 140360.4 | 80 | 168.9 | 746673.12 | 337.8 | 1493346.24 | 40 | 147360 | 168 | 618912 | 207 | 0 | 80 | 3684 | 175 | 3684 | 16 | 3684 | 96 | 3684 | 300 | 0 | 1034393.52 | 127156575.6 | 280.78 | 34515.9
67 | B.Z (Musa Pak) | ASHRAF ABAD | Rural | 4532 | 70 | 21 | 95172 | 29 | 78 | 424195.2 | 156 | 848390.4 | 6 | 27192 | 19 | 86108 | 99 | 0 | 80 | 4532 | 175 | 4532 | 16 | 0 | 96 | 0 | 300 | 0 | 546559.2 | 56355420 | 120.6 | 12435
68 | B.Z (Musa Pak) | NEW MUSA PAK | Rural | 2868 | 2509 | 752.7 | 2158743.6 | 71 | 1827.3 | 6288835.68 | 3654.6 | 12577671.36 | 159 | 456012 | 181.33 | 520054.44 | 2580 | 0 | 80 | 2868 | 175 | 2868 | 16 | 2868 | 96 | 2868 | 300 | 2868 | 8903591.28 | 792339778.8 | 3104.46 | 276269.1
69 | B.Z (Musa Pak) | JHOKE WAINS | Rural | 3092 | 1021 | 306.3 | 947079.6 | 100 | 814.7 | 3022862.88 | 1629.4 | 6045725.76 | 21 | 64932 | 51.35 | 158774.2 | 1121 | 0 | 80 | 3092 | 175 | 3092 | 16 | 3092 | 96 | 0 | 300 | 3092 | 4034874.48 | 375111236.4 | 1304.94 | 121316.7
70 | B.Z (Musa Pak) | MEHMOOD KOT | Rural | 6298 | 305 | 91.5 | 576267 | 54 | 267.5 | 2021658 | 535 | 4043316 | 39 | 245622 | 149.87 | 943881.26 | 359 | 0 | 80 | 6298 | 175 | 6298 | 16 | 6298 | 96 | 6298 | 300 | 0 | 2843547 | 300960636.6 | 451.5 | 47786.7
71 | B.Z (Musa Pak) | SALAR WAHIN | Rural | 4587 | 895 | 268.5 | 1231609.5 | 109 | 735.5 | 4048486.2 | 1471 | 8096972.4 | 13 | 59631 | 42.18 | 193479.66 | 1004 | 0 | 80 | 4587 | 175 | 4587 | 16 | 0 | 96 | 0 | 300 | 0 | 5339726.7 | 501121952.1 | 1164.1 | 109248.3
72 | B.Z (Musa Pak) | MUSA PAK | Rural | 506 | 103 | 30.9 | 15635.4 | 18 | 90.1 | 54708.72 | 180.2 | 109417.44 | 4 | 2024 | 21.45 | 10853.7 | 121 | 0 | 80 | 506 | 175 | 506 | 16 | 0 | 96 | 0 | 300 | 0 | 72368.12 | 7263174.6 | 143.02 | 14354.1
73 | B.Z (Musa Pak) | SANGHI | Rural | 6593 | 265 | 79.5 | 524143.5 | 43 | 228.5 | 1807800.6 | 457 | 3615601.2 | 8 | 52744 | 60.65 | 399865.45 | 308 | 0 | 80 | 6593 | 175 | 6593 | 16 | 0 | 96 | 0 | 300 | 0 | 2384688.1 | 242500429.5 | 361.7 | 36781.5
74 | B.Z (Musa Pak) | NEW BOSAN | Rural | 1400 | 319 | 95.7 | 133980 | 22 | 245.3 | 412104 | 490.6 | 824208 | 15 | 21000 | 39.3 | 55020 | 341 | 0 | 80 | 1400 | 175 | 1400 | 16 | 0 | 96 | 0 | 300 | 0 | 567084 | 53155620 | 405.06 | 37968.3
75 | B.Z (Musa Pak) | NEW SANGI | Rural | 7572 | 715 | 214.5 | 1624194 | 79 | 579.5 | 5265568.8 | 1159 | 10531137.6 | 263 | 1991436 | 292.19 | 2212462.68 | 794 | 0 | 80 | 7572 | 175 | 7572 | 16 | 7572 | 96 | 7572 | 300 | 0 | 8881198.8 | 769488598.8 | 1172.9 | 101622.9
76 | B.Z (Musa Pak) | SIDDIQUE ABAD | Rural | 4097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 0 | 0 | 0 | 0
77 | B.Z (Musa Pak) | NEW GARRAY WALA | Rural | 7808 | 174 | 52.2 | 407577.6 | 164 | 285.8 | 2677831.68 | 571.6 | 5355663.36 | 28 | 218624 | 93.2 | 727705.6 | 338 | 0 | 80 | 7808 | 175 | 7808 | 16 | 7808 | 96 | 0 | 300 | 0 | 3304033.28 | 366224870.4 | 423.16 | 46903.8
78 | B.Z (Musa Pak) | DARBAR PEER AKBAR SHAH | Rural | 6742 | 151 | 45.3 | 305412.6 | 151 | 256.7 | 2076805.68 | 513.4 | 4153611.36 | 22 | 148324 | 56.55 | 381260.1 | 302 | 0 | 80 | 6742 | 175 | 6742 | 16 | 6742 | 96 | 0 | 300 | 0 | 2530542.28 | 273008525.4 | 375.34 | 40493.7
79 | B.Z (Musa Pak) | MUHAMMAD PUR | Rural | 12533 | 41 | 12.3 | 154155.9 | 20 | 48.7 | 732428.52 | 97.4 | 1464857.04 | 10 | 125330 | 22.4 | 280739.2 | 61 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 1011914.42 | 105198242.1 | 80.74 | 8393.7
80 | S.R.Alam | TATA PUR | Rural | 6154 | 410 | 123 | 756942 | 26 | 313 | 2311442.4 | 626 | 4622884.8 | 20 | 123080 | 80.3 | 494166.2 | 436 | 0 | 80 | 6154 | 175 | 6154 | 16 | 6154 | 96 | 0 | 300 | 0 | 3191464.4 | 309293886 | 518.6 | 50259
81 | S.R.Alam | QURESHI | Rural | 6514 | 386 | 115.8 | 754321.2 | 25 | 295.2 | 2307519.36 | 590.4 | 4615038.72 | 40 | 260560 | 92.55 | 602870.7 | 411 | 0 | 80 | 6514 | 175 | 6514 | 16 | 6514 | 96 | 0 | 300 | 0 | 3322400.56 | 315337528.8 | 510.04 | 48409.2
82 | S.R.Alam | DOGAR | Rural | 7744 | 426 | 127.8 | 989683.2 | 92 | 390.2 | 3626050.56 | 780.4 | 7252101.12 | 8 | 61952 | 35 | 271040 | 518 | 1 | 80 | 7744 | 175 | 7744 | 16 | 0 | 96 | 0 | 300 | 0 | 4677685.76 | 454357516.8 | 604.04 | 58672.2
83 | S.R.Alam | RIAZ ABAD | Rural | 6246 | 311 | 93.3 | 582751.8 | 17 | 234.7 | 1759123.44 | 469.4 | 3518246.88 | 14 | 87444 | 78.95 | 493121.7 | 328 | 0 | 80 | 6246 | 175 | 6246 | 16 | 0 | 96 | 0 | 300 | 0 | 2429319.24 | 242430370.2 | 388.94 | 38813.7
84 | S.R.Alam | LOOTHER | Rural | 5005 | 246 | 73.8 | 369369 | 17 | 189.2 | 1136335.2 | 378.4 | 2272670.4 | 17 | 85085 | 71.97 | 360209.85 | 263 | 0 | 80 | 5005 | 175 | 5005 | 16 | 5005 | 96 | 0 | 300 | 0 | 1590789.2 | 159080922 | 317.84 | 31784.4
85 | S.R.Alam | RAWAN | Rural | 9004 | 233 | 69.9 | 629379.6 | 17 | 180.1 | 1945944.48 | 360.2 | 3891888.96 | 26 | 234104 | 63.83 | 574725.32 | 250 | 0 | 80 | 9004 | 175 | 9004 | 16 | 9004 | 96 | 0 | 300 | 0 | 2809428.08 | 269884995.6 | 312.02 | 29973.9
86 | S.R.Alam | MATITAL | Rural | 4775 | 270 | 81 | 386775 | 20 | 209 | 1197570 | 418 | 2395140 | 13 | 62075 | 84.85 | 405158.75 | 290 | 0 | 80 | 4775 | 175 | 4775 | 16 | 0 | 96 | 0 | 300 | 0 | 1646420 | 169178250 | 344.8 | 35430
87 | S.R.Alam | NEW MATTITAL | Rural | 4783 | 933 | 279.9 | 1338761.7 | 90 | 743.1 | 4265096.76 | 1486.2 | 8530193.52 | 362 | 1731446 | 391.23 | 1871253.09 | 1023 | 0 | 80 | 4783 | 175 | 4783 | 16 | 4783 | 96 | 4783 | 300 | 0 | 7335304.46 | 628103081.7 | 1533.62 | 131319.9
88 | S.R.Alam | PIRAN GHAIB | Rural | 6256 | 375 | 112.5 | 703800 | 142 | 404.5 | 3036662.4 | 809 | 6073324.8 | 27 | 168912 | 121 | 756976 | 517 | 0 | 80 | 6256 | 175 | 6256 | 16 | 6256 | 96 | 6256 | 300 | 0 | 3909374.4 | 411929448 | 624.9 | 65845.5
|  | TOTAL |  | 468756 | 32849 | 9854.7 | 53819409.3 | 6898 | 29892.3 | 194346172.44 | 59784.6 | 388692344.88 | 5665 | 29555830 | 8259.2222 | 43615759.2888 | 39744 | 4 | 80 | 452126 | 175 | 444536 | 16 | 285271 | 96 | 120308 | 300 | 13918 | 277721411.74 | 26099944478.025 | 592.4648 | 55679.1689

## 400-220 (Rural) DGKhan
Statement of 400/220 V MEPCO Consumers For 2020-21
D.G Khan Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder | Category | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | DG Khan | Sarwar Wali | Rural | 7038 | 603 | 180.9 | 1273174.2 | 134 | 556.1 | 4696598.16 | 1112.2 | 9393196.32 | 48 | 337824 | 103 | 724914 | 737 | 0 | 80 | 7038 | 175 | 7038 | 16 | 7038 | 96 | 7038 | 300 | 0 | 6307596.36 | 610906141.8 | 896.22 | 86801.1
2 | Kot Chutta | Chotti Bala | Rural | 709 | 236 | 70.8 | 50197.2 | 29 | 194.2 | 165225.36 | 388.4 | 330450.72 | 14 | 9926 | 52 | 36868 | 264 | 1 | 80 | 709 | 175 | 709 | 16 | 0 | 96 | 0 | 300 | 0 | 225348.56 | 22189714.8 | 317.84 | 31297.2
3 | Kot Chutta | Thatha Gabolan | Rural | 8717 | 443 | 132.9 | 1158489.3 | 74 | 384.1 | 4017839.64 | 768.2 | 8035679.28 | 284 | 2475628 | 508 | 4428236 | 516 | 1 | 80 | 8717 | 175 | 8717 | 16 | 8717 | 96 | 8717 | 300 | 0 | 7651956.94 | 751310384.7 | 877.82 | 86189.1
4 | Kot Chutta | Jhoke Utara | Rural | 7659 | 408 | 122.4 | 937461.6 | 105 | 390.6 | 3589926.48 | 781.2 | 7179852.96 | 97 | 742923 | 294 | 2251746 | 511 | 2 | 80 | 7659 | 175 | 7659 | 16 | 7659 | 96 | 7659 | 300 | 0 | 5270311.08 | 568708322.4 | 688.12 | 74253.6
5 | Kot Chutta | Shero | Rural | 5107 | 471 | 141.3 | 721619.1 | 85 | 414.7 | 2541447.48 | 829.4 | 5082894.96 | 115 | 587305 | 312 | 1593384 | 554 | 2 | 80 | 5107 | 175 | 5107 | 16 | 5107 | 96 | 5107 | 300 | 0 | 3850371.58 | 402741594.9 | 753.94 | 78860.7
6 | Kot Chutta | City Chotti | Rural | 4552 | 466 | 139.8 | 636369.6 | 13 | 339.2 | 1852846.08 | 678.4 | 3705692.16 | 53 | 241256 | 132 | 600864 | 479 | 0 | 80 | 4552 | 175 | 4552 | 16 | 4552 | 96 | 4552 | 300 | 0 | 2730471.68 | 260302478.4 | 599.84 | 57184.2
7 | Kot Chutta | Qaim Wala | Rural | 5761 | 879 | 263.7 | 1519175.7 | 20 | 635.3 | 4391955.96 | 1270.6 | 8783911.92 | 51 | 293811 | 167 | 962087 | 899 | 0 | 80 | 5761 | 175 | 5761 | 16 | 5761 | 96 | 5761 | 300 | 0 | 6204942.66 | 589317462.3 | 1077.06 | 102294.3
8 | Kot Chutta | Talpur | Rural | 5553 | 725 | 217.5 | 1207777.5 | 19 | 526.5 | 3508385.4 | 1053 | 7016770.8 | 22 | 122166 | 87 | 483111 | 744 | 0 | 80 | 5553 | 175 | 5553 | 16 | 5553 | 96 | 0 | 300 | 0 | 4838328.9 | 453616240.5 | 871.3 | 81688.5
9 | Kot Chutta | Leghari | Rural | 2730 | 791 | 237.3 | 647829 | 27 | 580.7 | 1902373.2 | 1161.4 | 3804746.4 | 29 | 79170 | 86 | 234780 | 818 | 0 | 80 | 2730 | 175 | 2730 | 16 | 2730 | 96 | 0 | 300 | 0 | 2629372.2 | 244315071 | 963.14 | 89492.7
10 | Kot Chutta | Airport | Rural | 839 | 379 | 113.7 | 95394.3 | 6 | 271.3 | 273144.84 | 542.6 | 546289.68 | 19 | 15941 | 60 | 50340 | 385 | 0 | 80 | 839 | 175 | 839 | 16 | 839 | 96 | 0 | 300 | 0 | 384480.14 | 36083963.7 | 458.26 | 43008.3
11 | Kot Chutta | Chak Birmani | Rural | 715 | 413 | 123.9 | 88588.5 | 3 | 292.1 | 250621.8 | 584.2 | 501243.6 | 17 | 12155 | 64 | 45760 | 416 | 0 | 80 | 715 | 175 | 715 | 16 | 715 | 96 | 0 | 300 | 0 | 351365.3 | 33085981.5 | 491.42 | 46274.1
12 | Kot Chutta | Chak Buzdar | Rural | 742 | 773 | 231.9 | 172069.8 | 16 | 557.1 | 496041.84 | 1114.2 | 992083.68 | 34 | 25228 | 118 | 87556 | 789 | 0 | 80 | 742 | 175 | 742 | 16 | 742 | 96 | 742 | 300 | 0 | 693339.64 | 65294590.2 | 934.42 | 87998.1
13 | Kot Chutta | Nawan Shaher | Rural | 3188 | 717 | 215.1 | 685738.8 | 14 | 515.9 | 1973627.04 | 1031.8 | 3947254.08 | 37 | 117956 | 120 | 382560 | 731 | 0 | 80 | 3188 | 175 | 3188 | 16 | 3188 | 96 | 3188 | 300 | 0 | 2777321.84 | 261846061.2 | 871.18 | 82134.9
14 | Kot Chutta | Ghaus Abad | Rural | 6848 | 485 | 145.5 | 996384 | 84 | 423.5 | 3480153.6 | 847 | 6960307.2 | 97 | 664256 | 257 | 1759936 | 567 | 2 | 80 | 6848 | 175 | 6848 | 16 | 6848 | 96 | 6848 | 300 | 0 | 5140793.6 | 526203744 | 750.7 | 76840.5
15 | Kot Chutta | Basti Jam | Rural | 4004 | 379 | 113.7 | 455254.8 | 71 | 336.3 | 1615854.24 | 672.6 | 3231708.48 | 89 | 356356 | 244 | 976976 | 448 | 2 | 80 | 4004 | 175 | 4004 | 16 | 4004 | 96 | 4004 | 300 | 0 | 2427465.04 | 253886833.2 | 606.26 | 63408.3
16 | Kot Chutta | Industrial | Rural | 2794 | 94 | 28.2 | 78790.8 | 17 | 82.8 | 277611.84 | 165.6 | 555223.68 | 60 | 167640 | 157 | 438658 | 111 | 0 | 80 | 2794 | 175 | 2794 | 16 | 2794 | 96 | 2794 | 300 | 0 | 524042.64 | 59869273.2 | 187.56 | 21427.8
17 | DG Khan | Paigah | Rural | 12672 | 530 | 159 | 2014848 | 211 | 582 | 8850124.8 | 1164 | 17700249.6 | 280 | 3548160 | 396 | 5018112 | 741 | 0 | 80 | 12672 | 175 | 12672 | 16 | 12672 | 96 | 12672 | 300 | 0 | 14413132.8 | 1369146240 | 1137.4 | 108045
18 | DG Khan | Qutta Road-I | Rural | 1396 | 280 | 84 | 117264 | 60 | 256 | 428851.2 | 512 | 857702.4 | 20 | 27920 | 55 | 76780 | 340 | 0 | 80 | 1396 | 175 | 1396 | 16 | 1396 | 96 | 0 | 300 | 0 | 574035.2 | 56420736 | 411.2 | 40416
19 | DG Khan | Qutta Road-II | Rural | 129 | 636 | 190.8 | 24613.2 | 42 | 487.2 | 75418.56 | 974.4 | 150837.12 | 14 | 1806 | 50 | 6450 | 678 | 0 | 80 | 129 | 175 | 129 | 16 | 0 | 96 | 0 | 300 | 0 | 101837.76 | 9511066.8 | 789.44 | 73729.2
20 | DG Khan | Jampur Road | Rural | 370 | 311 | 93.3 | 34521 | 57 | 274.7 | 121966.8 | 549.4 | 243933.6 | 24 | 8880 | 99 | 36630 | 368 | 0 | 80 | 370 | 175 | 370 | 16 | 370 | 96 | 370 | 300 | 0 | 165367.8 | 16937379 | 446.94 | 45776.7
21 | DG Khan | Dari Meero | Rural | 6132 | 470 | 141 | 864612 | 53 | 382 | 2810908.8 | 764 | 5621817.6 | 204 | 1250928 | 114 | 699048 | 521 | 2 | 80 | 6132 | 175 | 6132 | 16 | 6132 | 96 | 6132 | 300 | 0 | 4926448.8 | 381845772 | 803.4 | 62271
22 | DG Khan | Samina | Rural | 9997 | 357 | 107.1 | 1070678.7 | 121 | 370.9 | 4449464.76 | 741.8 | 8898929.52 | 738 | 7377786 | 858 | 8577426 | 478 | 0 | 80 | 9997 | 175 | 9997 | 16 | 9997 | 96 | 9997 | 300 | 0 | 12897929.46 | 1051793367.3 | 1290.18 | 105210.9
23 | DG Khan | Chit Sirkani | Rural | 5475 | 441 | 132.3 | 724342.5 | 93 | 401.7 | 2639169 | 803.4 | 5278338 | 1758 | 9625050 | 1765 | 9663375 | 532 | 2 | 80 | 5475 | 175 | 5475 | 16 | 5475 | 96 | 5475 | 300 | 0 | 12988561.5 | 898675807.5 | 2372.34 | 164141.7
24 | DG Khan | Sakhi Sarwar | Rural | 30094 | 1379 | 413.7 | 12449887.8 | 73 | 1038.3 | 37495920.24 | 2076.6 | 74991840.48 | 31 | 932914 | 104 | 3129776 | 1450 | 2 | 80 | 30094 | 175 | 30094 | 16 | 30094 | 96 | 30094 | 300 | 30094 | 50878722.04 | 4724646652.2 | 1690.66 | 156996.3
25 | DG Khan | Sakhi Sarwar-II | Rural | 4539 | 696 | 208.8 | 947743.2 | 88 | 575.2 | 3132999.36 | 1150.4 | 6265998.72 | 67 | 304113 | 135 | 612765 | 784 | 0 | 80 | 4539 | 175 | 4539 | 16 | 4539 | 96 | 4539 | 300 | 0 | 4384855.56 | 415569052.8 | 966.04 | 91555.2
26 | DG Khan | Fort Minro | Rural | 10030 | 69 | 20.7 | 207621 | 1 | 49.3 | 593374.8 | 98.6 | 1186749.6 | 2079 | 20852370 | 2108 | 21143240 | 69 | 1 | 80 | 0 | 175 | 0 | 16 | 10030 | 96 | 10030 | 300 | 0 | 21653365.8 | 1340422239 | 2158.86 | 133641.3
27 | DG Khan | Bawata | Rural | 67 | 43 | 12.9 | 864.3 | 1 | 31.1 | 2500.44 | 62.2 | 5000.88 | 731 | 48977 | 750 | 50250 | 43 | 1 | 80 | 0 | 175 | 0 | 16 | 67 | 96 | 67 | 300 | 0 | 52341.74 | 3317645.7 | 781.22 | 49517.1
28 | DG Khan | Bawata-II | Rural | 249 | 60 | 18 | 4482 | 0 | 42 | 12549.6 | 84 | 25099.2 | 2191 | 545559 | 2214 | 551286 | 60 | 0 | 80 | 0 | 175 | 0 | 16 | 249 | 96 | 249 | 300 | 0 | 562590.6 | 34596558 | 2259.4 | 138942
29 | DG Khan | Anari | Rural | 792 | 79 | 23.7 | 18770.4 | 4 | 59.3 | 56358.72 | 118.6 | 112717.44 | 1645 | 1302840 | 1667 | 1320264 | 82 | 1 | 80 | 792 | 175 | 0 | 16 | 792 | 96 | 792 | 300 | 0 | 1377969.12 | 86035197.6 | 1739.86 | 108630.3
30 | DG Khan | Wador | Rural | 3184 | 529 | 158.7 | 505300.8 | 125 | 495.3 | 1892442.24 | 990.6 | 3784884.48 | 23 | 73232 | 73 | 232432 | 654 | 0 | 80 | 3184 | 175 | 3184 | 16 | 3184 | 96 | 0 | 300 | 0 | 2470975.04 | 242554891.2 | 776.06 | 76179.3
31 | DG Khan | Dari Dholy wali | Rural | 5163 | 1188 | 356.4 | 1840093.2 | 63 | 894.6 | 5542583.76 | 1789.2 | 11085167.52 | 250 | 1290750 | 311 | 1605693 | 1250 | 1 | 80 | 5163 | 175 | 5163 | 16 | 5163 | 96 | 5163 | 300 | 5163 | 8673426.96 | 766971910.8 | 1679.92 | 148551.6
32 | DG Khan | S.S.Din | Rural | 4206 | 374 | 112.2 | 471913.2 | 68 | 329.8 | 1664566.56 | 659.6 | 3329133.12 | 24 | 100944 | 83 | 349098 | 441 | 1 | 80 | 4206 | 175 | 4206 | 16 | 4206 | 96 | 0 | 300 | 0 | 2237423.76 | 222109606.8 | 531.96 | 52807.8
33 | DG Khan | Pir Adil | Rural | 6834 | 1436 | 430.8 | 2944087.2 | 66 | 1071.2 | 8784696.96 | 2142.4 | 17569393.92 | 509 | 3478506 | 568 | 3881712 | 1501 | 1 | 80 | 6834 | 175 | 6834 | 16 | 6834 | 96 | 6834 | 300 | 6834 | 15207290.16 | 1295898616.8 | 2225.24 | 189625.2
34 | DG Khan | Laden | Rural | 5497 | 863 | 258.9 | 1423173.3 | 69 | 673.1 | 4440036.84 | 1346.2 | 8880073.68 | 1247 | 6854759 | 1305 | 7173585 | 931 | 1 | 80 | 5497 | 175 | 5497 | 16 | 5497 | 96 | 5497 | 300 | 0 | 12717969.14 | 967489040.7 | 2313.62 | 176003.1
35 | DG Khan | Bahadur Garh | Rural | 4964 | 1354 | 406.2 | 2016376.8 | 55 | 1002.8 | 5973479.04 | 2005.6 | 11946958.08 | 537 | 2665668 | 600 | 2978400 | 1408 | 1 | 80 | 4964 | 175 | 4964 | 16 | 4964 | 96 | 4964 | 300 | 4964 | 10655523.84 | 901570615.2 | 2146.56 | 181621.8
36 | DG Khan | Chabri Bala | Rural | 7684 | 879 | 263.7 | 2026270.8 | 130 | 745.3 | 6872262.24 | 1490.6 | 13744524.48 | 27 | 207468 | 65 | 499460 | 1008 | 1 | 80 | 7684 | 175 | 7684 | 16 | 7684 | 96 | 0 | 300 | 0 | 9106001.04 | 860717881.2 | 1185.06 | 112014.3
37 | Rajanpur | Shikar Pur | Rural | 5407 | 877 | 263.1 | 1422581.7 | 80 | 693.9 | 4502300.76 | 1387.8 | 9004601.52 | 384 | 2076288 | 395 | 2135765 | 957 | 0 | 80 | 5407 | 175 | 5407 | 16 | 5407 | 96 | 5407 | 300 | 0 | 8001170.46 | 672689736.3 | 1479.78 | 124410.9
38 | Rajanpur | Kotla Essan | Rural | 1000 | 281 | 84.3 | 84300 | 41 | 237.7 | 285240 | 475.4 | 570480 | 78 | 78000 | 76 | 76000 | 322 | 0 | 80 | 1000 | 175 | 1000 | 16 | 1000 | 96 | 0 | 300 | 0 | 447540 | 39041700 | 447.54 | 39041.7
39 | Kot Chutta | Khanpur | Rural | 4241 | 713 | 213.9 | 907149.9 | 82 | 581.1 | 2957334.12 | 1162.2 | 5914668.24 | 194 | 822754 | 240 | 1017840 | 793 | 2 | 80 | 4241 | 175 | 4241 | 16 | 4241 | 96 | 4241 | 300 | 0 | 4687238.02 | 418671944.1 | 1105.22 | 98720.1
40 | Kot Chutta | Basti Fouja | Rural | 4083 | 884 | 265.2 | 1082811.6 | 144 | 762.8 | 3737414.88 | 1525.6 | 7474829.76 | 209 | 853347 | 252 | 1028916 | 1025 | 3 | 80 | 4083 | 175 | 4083 | 16 | 4083 | 96 | 4083 | 300 | 0 | 5673573.48 | 513473180.4 | 1389.56 | 125758.8
41 | Rajanpur | Murghai | Rural | 6851 | 843 | 252.9 | 1732617.9 | 61 | 651.1 | 5352823.32 | 1302.2 | 10705646.64 | 215 | 1472965 | 205 | 1404455 | 904 | 0 | 80 | 6851 | 175 | 6851 | 16 | 6851 | 96 | 6851 | 300 | 0 | 8558406.22 | 731803952.1 | 1249.22 | 106817.1
42 | Rajanpur | Bait Sontra | Rural | 3869 | 507 | 152.1 | 588474.9 | 64 | 418.9 | 1944868.92 | 837.8 | 3889737.84 | 379 | 1466351 | 381 | 1474089 | 571 | 0 | 80 | 3869 | 175 | 3869 | 16 | 3869 | 96 | 3869 | 300 | 0 | 3999694.82 | 323595035.1 | 1033.78 | 83637.9
43 | Rajanpur | Hajipur | Rural | 4836 | 1333 | 399.9 | 1933916.4 | 101 | 1034.1 | 6001089.12 | 2068.2 | 12002178.24 | 687 | 3322332 | 1009 | 4879524 | 1434 | 0 | 80 | 4836 | 175 | 4836 | 16 | 4836 | 96 | 4836 | 300 | 4836 | 11257337.52 | 1018703883.6 | 2327.82 | 210650.1
44 | Rajanpur | Raikh Bagh Wala | Rural | 3069 | 1320 | 396 | 1215324 | 72 | 996 | 3668068.8 | 1992 | 7336137.6 | 636 | 1951884 | 672 | 2062368 | 1392 | 0 | 80 | 3069 | 175 | 3069 | 16 | 3069 | 96 | 3069 | 300 | 3069 | 6835276.8 | 567556308 | 2227.2 | 184932
45 | Rajanpur | Adda Chiragh Shah | Rural | 476 | 570 | 171 | 81396 | 51 | 450 | 257040 | 900 | 514080 | 673 | 320348 | 743 | 353668 | 621 | 0 | 80 | 476 | 175 | 476 | 16 | 476 | 96 | 476 | 300 | 0 | 658784 | 52309068 | 1384 | 109893
46 | Rajanpur | Sahan Wala | Rural | 3359 | 908 | 272.4 | 914991.6 | 87 | 722.6 | 2912656.08 | 1445.2 | 5825312.16 | 974 | 3271666 | 1023 | 3436257 | 992 | 3 | 80 | 3359 | 175 | 3359 | 16 | 3359 | 96 | 3359 | 300 | 0 | 7099313.68 | 558439124.4 | 2113.52 | 166251.6
47 | Rajanpur | Mehrey Wala | Rural | 3702 | 837 | 251.1 | 929572.2 | 75 | 660.9 | 2935982.16 | 1321.8 | 5871964.32 | 615 | 2276730 | 656 | 2428512 | 906 | 6 | 80 | 3702 | 175 | 3702 | 16 | 3702 | 96 | 3702 | 300 | 0 | 6142284.36 | 500817295.8 | 1659.18 | 135282.9
48 | Rajanpur | Laal Garh | Rural | 2300 | 8 | 2.4 | 5520 | 18 | 23.6 | 65136 | 47.2 | 130272 | 41 | 94300 | 63 | 144900 | 26 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 164956 | 16526880 | 71.72 | 7185.6
49 | Rajanpur | Q/Abad | Rural | 2882 | 1355 | 406.5 | 1171533 | 50 | 998.5 | 3453212.4 | 1997 | 6906424.8 | 672 | 1936704 | 701 | 2020282 | 1405 | 0 | 80 | 2882 | 175 | 2882 | 16 | 2882 | 96 | 2882 | 300 | 2882 | 6561449.4 | 539117007 | 2276.7 | 187063.5
50 | Kot Chutta | M.Pur | Rural | 4363 | 1269 | 380.7 | 1660994.1 | 91 | 979.3 | 5127223.08 | 1958.6 | 10254446.16 | 212 | 924956 | 240 | 1047120 | 1360 | 0 | 80 | 4363 | 175 | 4363 | 16 | 4363 | 96 | 4363 | 300 | 4363 | 7713173.18 | 683076951.9 | 1767.86 | 156561.3
51 | Rajanpur | Dajal | Rural | 6536 | 1808 | 542.4 | 3545126.4 | 31 | 1296.6 | 10169493.12 | 2593.2 | 20338986.24 | 15 | 98040 | 45 | 294120 | 1839 | 0 | 80 | 6536 | 175 | 6536 | 16 | 0 | 96 | 0 | 300 | 6536 | 13812659.52 | 1248621753.6 | 2113.32 | 191037.6
52 | Rajanpur | Harand | Rural | 1982 | 887 | 266.1 | 527410.2 | 68 | 688.9 | 1638479.76 | 1377.8 | 3276959.52 | 17 | 33694 | 53 | 105046 | 955 | 0 | 80 | 1982 | 175 | 1982 | 16 | 1982 | 96 | 0 | 300 | 0 | 2199583.96 | 204502561.8 | 1109.78 | 103179.9
53 | Rajanpur | Noshera | Rural | 3430 | 1231 | 369.3 | 1266699 | 65 | 926.7 | 3814297.2 | 1853.4 | 7628594.4 | 138 | 473340 | 173 | 593390 | 1296 | 0 | 80 | 3430 | 175 | 3430 | 16 | 3430 | 96 | 3430 | 300 | 3430 | 5554336.2 | 497119161 | 1619.34 | 144932.7
54 | Kot Chutta | Kotla Mughlan | Rural | 3766 | 1127 | 338.1 | 1273284.6 | 120 | 908.9 | 4107500.88 | 1817.8 | 8215001.76 | 38 | 143108 | 111 | 418026 | 1247 | 0 | 80 | 3766 | 175 | 3766 | 16 | 3766 | 96 | 3766 | 300 | 3766 | 5523893.48 | 521801519.4 | 1466.78 | 138555.9
55 | Kot Chutta | Bukhara | Rural | 4046 | 1644 | 493.2 | 1995487.2 | 117 | 1267.8 | 6155422.56 | 2535.6 | 12310845.12 | 39 | 157794 | 115 | 465290 | 1761 | 0 | 80 | 4046 | 175 | 4046 | 16 | 4046 | 96 | 4046 | 300 | 4046 | 8308703.76 | 772554568.8 | 2053.56 | 190942.8
56 | Kot Chutta | Jhakar Chowk | Rural | 951 | 227 | 68.1 | 64763.1 | 53 | 211.9 | 241820.28 | 423.8 | 483640.56 | 756 | 718956 | 777 | 738927 | 278 | 2 | 80 | 951 | 175 | 951 | 16 | 951 | 96 | 951 | 300 | 0 | 1025539.38 | 73548342.9 | 1078.38 | 77337.9
57 | Kot Chutta | Indus | Rural | 2716 | 459 | 137.7 | 373993.2 | 62 | 383.3 | 1249251.36 | 766.6 | 2498502.72 | 181 | 491596 | 244 | 662704 | 521 | 0 | 80 | 2716 | 175 | 2716 | 16 | 2716 | 96 | 2716 | 300 | 0 | 2114840.56 | 190794382.8 | 778.66 | 70248.3
58 | Kot Chutta | Industrial | Rural | 4369 | 1087 | 326.1 | 1424730.9 | 61 | 821.9 | 4309057.32 | 1643.8 | 8618114.64 | 510 | 2228190 | 530 | 2315570 | 1148 | 0 | 80 | 4369 | 175 | 4369 | 16 | 4369 | 96 | 4369 | 300 | 4369 | 7961978.22 | 660295271.1 | 1822.38 | 151131.9
59 | Rajanpur | Rojhan | Rural | 4068 | 836 | 250.8 | 1020254.4 | 93 | 678.2 | 3310701.12 | 1356.4 | 6621402.24 | 56 | 227808 | 76 | 309168 | 926 | 3 | 80 | 4068 | 175 | 4068 | 16 | 4068 | 96 | 0 | 300 | 0 | 4558763.52 | 418894977.6 | 1120.64 | 102973.2
60 | Rajanpur | Dilbar | Rural | 2402 | 1314 | 394.2 | 946868.4 | 57 | 976.8 | 2815528.32 | 1953.6 | 5631056.64 | 1142 | 2743084 | 1167 | 2803134 | 1365 | 6 | 80 | 2402 | 175 | 2402 | 16 | 2402 | 96 | 2402 | 300 | 2402 | 6505480.72 | 508892043.6 | 2708.36 | 211861.8
61 | Rajanpur | Umer Kot | Rural | 3632 | 1112 | 333.6 | 1211635.2 | 62 | 840.4 | 3662799.36 | 1680.8 | 7325598.72 | 1177 | 4274864 | 1104 | 4009728 | 1161 | 13 | 80 | 3632 | 175 | 3632 | 16 | 3632 | 96 | 3632 | 300 | 3632 | 9149298.56 | 683754508.8 | 2519.08 | 188258.4
62 | Rajanpur | Meeran Pur | Rural | 1342 | 1144 | 343.2 | 460574.4 | 79 | 879.8 | 1416829.92 | 1759.6 | 2833659.84 | 10 | 13420 | 33 | 44286 | 1221 | 2 | 80 | 1342 | 175 | 1342 | 16 | 0 | 96 | 0 | 300 | 1342 | 1890824.32 | 174058473.6 | 1408.96 | 129700.8
63 | Taunsa | Karim Wala | Rural | 5295 | 2264 | 679.2 | 3596364 | 35 | 1619.8 | 10292209.2 | 3239.6 | 20584418.4 | 159 | 841905 | 381 | 2017395 | 2299 | 0 | 80 | 5295 | 175 | 5295 | 16 | 5295 | 96 | 5295 | 300 | 5295 | 14730478.2 | 1366897896 | 2781.96 | 258148.8
64 | Taunsa | Nari | Rural | 4991 | 418 | 125.4 | 625871.4 | 33 | 325.6 | 1950083.52 | 651.2 | 3900167.04 | 33 | 164703 | 98 | 489118 | 451 | 0 | 80 | 4991 | 175 | 4991 | 16 | 4991 | 96 | 4991 | 300 | 0 | 2740657.92 | 265234716.6 | 549.12 | 53142.6
65 | Taunsa | Gypsum | Rural | 10021 | 581 | 174.3 | 1746660.3 | 23 | 429.7 | 5167228.44 | 859.4 | 10334456.88 | 171 | 1713591 | 397 | 3978337 | 604 | 0 | 80 | 10021 | 175 | 10021 | 16 | 10021 | 96 | 10021 | 300 | 0 | 8627479.74 | 864007613.7 | 860.94 | 86219.7
66 | Taunsa | Kot Qaisrani | Rural | 7705 | 640 | 192 | 1479360 | 18 | 466 | 4308636 | 932 | 8617272 | 102 | 785910 | 213 | 1641165 | 658 | 0 | 80 | 7705 | 175 | 7705 | 16 | 7705 | 96 | 7705 | 300 | 0 | 6573906 | 619944300 | 853.2 | 80460
67 | Taunsa | Nizam Abad | Rural | 6870 | 141 | 42.3 | 290601 | 24 | 122.7 | 1011538.8 | 245.4 | 2023077.6 | 66 | 453420 | 157 | 1078590 | 165 | 0 | 80 | 6870 | 175 | 6870 | 16 | 6870 | 96 | 6870 | 300 | 0 | 1755559.8 | 186971859 | 255.54 | 27215.7
68 | Taunsa | Jatt Wala | Rural | 5177 | 146 | 43.8 | 226752.6 | 14 | 116.2 | 721880.88 | 232.4 | 1443761.76 | 23 | 119071 | 76 | 393452 | 160 | 0 | 80 | 5177 | 175 | 5177 | 16 | 5177 | 96 | 0 | 300 | 0 | 1067704.48 | 110913083.4 | 206.24 | 21424.2
69 | Taunsa | New Kot Qaisrani | Rural | 6420 | 574 | 172.2 | 1105524 | 26 | 427.8 | 3295771.2 | 855.6 | 6591542.4 | 146 | 937320 | 206 | 1322520 | 600 | 0 | 80 | 6420 | 175 | 6420 | 16 | 6420 | 96 | 6420 | 300 | 0 | 5338615.2 | 478160316 | 831.56 | 74479.8
70 | Taunsa | Shaden Lund | Rural | 6706 | 760 | 228 | 1528968 | 38 | 570 | 4586904 | 1140 | 9173808 | 262 | 1756972 | 379 | 2541574 | 798 | 0 | 80 | 6706 | 175 | 6706 | 16 | 6706 | 96 | 6706 | 300 | 0 | 7872844 | 707509824 | 1174 | 105504
71 | Taunsa | Taunsa Barrage | Rural | 4897 | 503 | 150.9 | 738957.3 | 39 | 391.1 | 2298260.04 | 782.2 | 4596520.08 | 399 | 1953903 | 485 | 2375045 | 542 | 0 | 80 | 4897 | 175 | 4897 | 16 | 4897 | 96 | 4897 | 300 | 0 | 4991120.34 | 420510776.7 | 1019.22 | 85871.1
72 | Taunsa | Zinda Peer | Rural | 1182 | 594 | 178.2 | 210632.4 | 22 | 437.8 | 620975.52 | 875.6 | 1241951.04 | 84 | 99288 | 142 | 167844 | 616 | 0 | 80 | 1182 | 175 | 1182 | 16 | 1182 | 96 | 1182 | 300 | 0 | 930895.92 | 85219599.6 | 787.56 | 72097.8
73 | Taunsa | Kala | Rural | 8229 | 1026 | 307.8 | 2532886.2 | 62 | 780.2 | 7704318.96 | 1560.4 | 15408637.92 | 426 | 3505554 | 599 | 4929171 | 1088 | 0 | 80 | 8229 | 175 | 8229 | 16 | 8229 | 96 | 8229 | 300 | 8229 | 13742759.16 | 1227867193.8 | 1670.04 | 149212.2
74 | Taunsa | Kot Mohi | Rural | 1972 | 1106 | 331.8 | 654309.6 | 69 | 843.2 | 1995348.48 | 1686.4 | 3990696.96 | 119 | 234668 | 266 | 524552 | 1175 | 0 | 80 | 1972 | 175 | 1972 | 16 | 1972 | 96 | 1972 | 300 | 1972 | 2884326.08 | 272877866.4 | 1462.64 | 138376.2
75 | Taunsa | Tibbi Qaisrani |  | 9209 | 924 | 277.2 | 2552734.8 | 41 | 687.8 | 7600740.24 | 1375.6 | 15201480.48 | 51 | 469659 | 96 | 884064 | 964 | 1 | 80 | 9209 | 175 | 9209 | 16 | 9209 | 96 | 0 | 300 | 0 | 10623134.04 | 972790873.2 | 1153.56 | 105634.8
76 | Taunsa | New Tibbi Qaisrani |  | 5041 | 782 | 234.6 | 1182618.6 | 47 | 594.4 | 3595644.48 | 1188.8 | 7191288.96 | 57 | 287337 | 132 | 665412 | 828 | 1 | 80 | 5041 | 175 | 5041 | 16 | 5041 | 96 | 5041 | 300 | 0 | 5065600.08 | 474949913.4 | 1004.88 | 94217.4
77 | Taunsa | Raitra |  | 7420 | 319 | 95.7 | 710094 | 40 | 263.3 | 2344423.2 | 526.6 | 4688846.4 | 45 | 333900 | 65 | 482300 | 357 | 2 | 80 | 7420 | 175 | 7420 | 16 | 7420 | 96 | 0 | 300 | 0 | 3388417.2 | 312399066 | 456.66 | 42102.3
78 | Taunsa | Noor Ahmad Wali |  | 732 | 433 | 129.9 | 95086.8 | 37 | 340.1 | 298743.84 | 680.2 | 597487.68 | 51 | 37332 | 108 | 79056 | 469 | 1 | 80 | 732 | 175 | 732 | 16 | 732 | 96 | 732 | 300 | 0 | 431162.64 | 40877881.2 | 589.02 | 55844.1
79 | Taunsa | Mehmoodia |  | 8331 | 601 | 180.3 | 1502079.3 | 23 | 443.7 | 4435757.64 | 887.4 | 8871515.28 | 129 | 1074699 | 269 | 2241039 | 624 | 0 | 80 | 8331 | 175 | 8331 | 16 | 8331 | 96 | 8331 | 300 | 0 | 7012535.94 | 671259494.7 | 841.74 | 80573.7
80 | Taunsa | Bathi |  | 2034 | 1122 | 336.6 | 684644.4 | 36 | 821.4 | 2004873.12 | 1642.8 | 4009746.24 | 207 | 421038 | 237 | 482058 | 1157 | 1 | 80 | 2034 | 175 | 2034 | 16 | 2034 | 96 | 2034 | 300 | 2034 | 3110555.52 | 271562187.6 | 1529.28 | 133511.4
81 | Taunsa | Jaloo Wali |  | 4099 | 490 | 147 | 602553 | 28 | 371 | 1824874.8 | 742 | 3649749.6 | 39 | 159861 | 82 | 336118 | 517 | 1 | 80 | 4099 | 175 | 4099 | 16 | 4099 | 96 | 0 | 300 | 0 | 2587288.8 | 240959715 | 631.2 | 58785
|  | TOTAL |  | 345573 | 53570 | 16071 | 83010674.7 | 4385 | 41884 | 260918053.56 | 83768 | 521836107.12 | 25503 | 111786995 | 31553 | 140391406 | 62806 | 65 | 80 | 332927 | 175 | 332135 | 16 | 334557 | 96 | 296023 | 300 | 107224 | 455715723.26 | 39982682811.3 | 1318.7249 | 115699.6722

## 400-220 (Rural) Vehari
Statement of 400/220 V MEPCO Consumers For 2020-21
Vehari Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | Vehari | Ratta Tibba | Rural | 2319 | 243 | 72.9 | 169055.1 | 19 | 189.1 | 526227.48 | 378.2 | 1052454.96 | 24 | 55656 | 33 | 76527 | 262 | 0 | 80 | 2319 | 175 | 2319 | 16 | 2319 | 96 | 0 | 300 | 0 | 750938.58 | 68246082.9 | 323.82 | 29429.1
2 | Vehari | Machiwala(M.Pakhi) | Rural | 10715 | 363 | 108.9 | 1166863.5 | 9 | 263.1 | 3382939.8 | 526.2 | 6765879.6 | 31 | 332165 | 35 | 375025 | 372 | 0 | 80 | 10715 | 175 | 10715 | 16 | 10715 | 96 | 0 | 300 | 0 | 4881968.3 | 431954866.5 | 455.62 | 40313.1
3 | Vehari | Dana Ibrahim | Rural | 4222 | 190 | 57 | 240654 | 11 | 144 | 729561.6 | 288 | 1459123.2 | 27 | 113994 | 41 | 173102 | 201 | 0 | 80 | 4222 | 175 | 4222 | 16 | 4222 | 96 | 0 | 300 | 0 | 1084209.6 | 98655474 | 256.8 | 23367
4 | Vehari | Liaqat Shaheed | Rural | 5193 | 254 | 76.2 | 395706.6 | 7 | 184.8 | 1151599.68 | 369.6 | 2303199.36 | 25 | 129825 | 42 | 218106 | 261 | 0 | 80 | 5193 | 175 | 5193 | 16 | 5193 | 96 | 0 | 300 | 0 | 1677131.28 | 152465441.4 | 322.96 | 29359.8
5 | Vehari | Chak-37W/B Old | Rural | 6552 | 344 | 103.2 | 676166.4 | 18 | 258.8 | 2034789.12 | 517.6 | 4069578.24 | 44 | 288288 | 59 | 386568 | 362 | 0 | 80 | 6552 | 175 | 6552 | 16 | 6552 | 96 | 0 | 300 | 0 | 2999243.52 | 269397273.6 | 457.76 | 41116.8
6 | Vehari | Chak-22/W.B | Rural | 6281 | 497 | 149.1 | 936497.1 | 21 | 368.9 | 2780473.08 | 737.8 | 5560946.16 | 29 | 182149 | 36 | 226116 | 518 | 0 | 80 | 6281 | 175 | 6281 | 16 | 6281 | 96 | 0 | 300 | 0 | 3899119.18 | 350033220.9 | 620.78 | 55728.9
7 | Vehari | Chak-182/E.B | Rural | 6870 | 264 | 79.2 | 544104 | 12 | 196.8 | 1622419.2 | 393.6 | 3244838.4 | 23 | 158010 | 22 | 151140 | 276 | 0 | 80 | 6870 | 175 | 6870 | 16 | 6870 | 96 | 0 | 300 | 0 | 2324533.2 | 205391016 | 338.36 | 29896.8
8 | Vehari | Jungle Burali | Rural | 6100 | 180 | 54 | 329400 | 8 | 134 | 980880 | 268 | 1961760 | 11 | 67100 | 17 | 103700 | 188 | 0 | 80 | 6100 | 175 | 6100 | 16 | 0 | 96 | 0 | 300 | 0 | 1377380 | 124915800 | 225.8 | 20478
9 | Vehari | Tipu | Rural | 4335 | 499 | 149.7 | 648949.5 | 33 | 382.3 | 1988724.6 | 764.6 | 3977449.2 | 68 | 294780 | 140 | 606900 | 532 | 0 | 80 | 4335 | 175 | 4335 | 16 | 4335 | 96 | 4335 | 300 | 0 | 2932454.1 | 277007800.5 | 676.46 | 63900.3
10 | Vehari | Muhammad Shah | Rural | 4020 | 406 | 121.8 | 489636 | 13 | 297.2 | 1433692.8 | 594.4 | 2867385.6 | 44 | 176880 | 121 | 486420 | 419 | 0 | 80 | 4020 | 175 | 4020 | 16 | 4020 | 96 | 4020 | 300 | 0 | 2100208.8 | 202697244 | 522.44 | 50422.2
11 | Vehari | Idrees Shaheed | Rural | 3374 | 296 | 88.8 | 299611.2 | 6 | 213.2 | 863204.16 | 426.4 | 1726408.32 | 35 | 118090 | 91 | 307034 | 302 | 0 | 80 | 3374 | 175 | 3374 | 16 | 3374 | 96 | 0 | 300 | 0 | 1280905.36 | 122905372.8 | 379.64 | 36427.2
12 | Vehari | Noor shah | Rural | 4337 | 231 | 69.3 | 300554.1 | 12 | 173.7 | 904004.28 | 347.4 | 1808008.56 | 32 | 138784 | 70 | 303590 | 243 | 0 | 80 | 4337 | 175 | 4337 | 16 | 4337 | 96 | 0 | 300 | 0 | 1343342.38 | 127597575.9 | 309.74 | 29420.7
13 | Vehari | New Chak-37/ W.B | Rural | 4786 | 267 | 80.1 | 383358.6 | 8 | 194.9 | 1119349.68 | 389.8 | 2238699.36 | 34 | 162724 | 64 | 306304 | 275 | 0 | 80 | 4786 | 175 | 4786 | 16 | 4786 | 96 | 0 | 300 | 0 | 1665432.28 | 153850277.4 | 347.98 | 32145.9
14 | Vehari | Shatab Garh | Rural | 7023 | 406 | 121.8 | 855401.4 | 18 | 302.2 | 2546820.72 | 604.4 | 5093641.44 | 53 | 372219 | 81 | 568863 | 424 | 0 | 80 | 7023 | 175 | 7023 | 16 | 7023 | 96 | 0 | 300 | 0 | 3774441.12 | 342316470.6 | 537.44 | 48742.2
15 | Vehari | Bashir Shaheed | Rural | 6397 | 200 | 60 | 383820 | 9 | 149 | 1143783.6 | 298 | 2287567.2 | 48 | 307056 | 58 | 371026 | 209 | 0 | 80 | 6397 | 175 | 6397 | 16 | 6397 | 96 | 0 | 300 | 0 | 1834659.6 | 160667052 | 286.8 | 25116
16 | Vehari | Ghulam Hussain | Rural | 9542 | 274 | 82.2 | 784352.4 | 6 | 197.8 | 2264889.12 | 395.6 | 4529778.24 | 19 | 181298 | 30 | 286260 | 280 | 0 | 80 | 9542 | 175 | 9542 | 16 | 9542 | 96 | 0 | 300 | 0 | 3230539.52 | 291315351.6 | 338.56 | 30529.8
17 | Vehari | MES Thingi | Rural | 6861 | 284 | 85.2 | 584557.2 | 25 | 223.8 | 1842590.16 | 447.6 | 3685180.32 | 44 | 301884 | 64 | 439104 | 309 | 0 | 80 | 6861 | 175 | 6861 | 16 | 6861 | 96 | 0 | 300 | 0 | 2729031.36 | 249210730.8 | 397.76 | 36322.8
18 | Vehari | Piply | Rural | 7313 | 280 | 84 | 614292 | 35 | 231 | 2027163.6 | 462 | 4054327.2 | 50 | 365650 | 71 | 519223 | 315 | 0 | 80 | 7313 | 175 | 7313 | 16 | 7313 | 96 | 0 | 300 | 0 | 3007105.6 | 276255888 | 411.2 | 37776
19 | Vehari | Khalil Shaheed | Rural | 4251 | 258 | 77.4 | 329027.4 | 33 | 213.6 | 1089616.32 | 427.2 | 2179232.64 | 48 | 204048 | 71 | 301821 | 291 | 0 | 80 | 4251 | 175 | 4251 | 16 | 4251 | 96 | 0 | 300 | 0 | 1622691.72 | 149850300.6 | 381.72 | 35250.6
20 | Vehari | 24/WB | Rural | 7193 | 350 | 105 | 755265 | 58 | 303 | 2615374.8 | 606 | 5230749.6 | 98 | 704914 | 108 | 776844 | 408 | 0 | 80 | 7193 | 175 | 7193 | 16 | 7193 | 96 | 7193 | 300 | 0 | 4075553.8 | 362721411 | 566.6 | 50427
21 | Vehari | Akram Shaheed | Rural | 6496 | 338 | 101.4 | 658694.4 | 46 | 282.6 | 2202923.52 | 565.2 | 4405847.04 | 75 | 487200 | 100 | 649600 | 384 | 0 | 80 | 6496 | 175 | 6496 | 16 | 6496 | 96 | 6496 | 300 | 0 | 3348817.92 | 305302905.6 | 515.52 | 46998.6
22 | Vehari | Hassan Shah | Rural | 2188 | 570 | 171 | 374148 | 6 | 405 | 1063368 | 810 | 2126736 | 57 | 124716 | 151 | 330388 | 576 | 0 | 80 | 2188 | 175 | 2188 | 16 | 2188 | 96 | 2188 | 300 | 0 | 1562232 | 148549884 | 714 | 67893
23 | Vehari | Tabarak Wah | Rural | 2160 | 338 | 101.4 | 219024 | 4 | 240.6 | 623635.2 | 481.2 | 1247270.4 | 32 | 69120 | 86 | 185760 | 342 | 0 | 80 | 2160 | 175 | 2160 | 16 | 2160 | 96 | 0 | 300 | 0 | 911779.2 | 86638896 | 422.12 | 40110.6
24 | Vehari | Ludden | Rural | 7774 | 536 | 160.8 | 1250059.2 | 27 | 402.2 | 3752043.36 | 804.4 | 7504086.72 | 59 | 458666 | 72 | 559728 | 563 | 0 | 80 | 7774 | 175 | 7774 | 16 | 7774 | 96 | 0 | 300 | 0 | 5460768.56 | 487579060.8 | 702.44 | 62719.2
25 | Vehari | Firdous | Rural | 3297 | 326 | 97.8 | 322446.6 | 16 | 244.2 | 966152.88 | 488.4 | 1932305.76 | 11 | 36267 | 24 | 79128 | 342 | 0 | 80 | 3297 | 175 | 3297 | 16 | 0 | 96 | 0 | 300 | 0 | 1324866.48 | 121653365.4 | 401.84 | 36898.2
26 | Vehari | Sajwar Shaheed | Rural | 2044 | 204 | 61.2 | 125092.8 | 4 | 146.8 | 360071.04 | 293.6 | 720142.08 | 15 | 30660 | 42 | 85848 | 208 | 0 | 80 | 2044 | 175 | 2044 | 16 | 0 | 96 | 0 | 300 | 0 | 515823.84 | 48734683.2 | 252.36 | 23842.8
27 | Vehari | Farooq Shaheed | Rural | 3477 | 290 | 87 | 302499 | 4 | 207 | 863686.8 | 414 | 1727373.6 | 19 | 66063 | 41 | 142557 | 294 | 0 | 80 | 3477 | 175 | 3477 | 16 | 3477 | 96 | 0 | 300 | 0 | 1232248.8 | 113103333 | 354.4 | 32529
28 | Vehari | Ahmed Abad | Rural | 3906 | 311 | 93.3 | 364429.8 | 12 | 229.7 | 1076649.84 | 459.4 | 2153299.68 | 18 | 70308 | 41 | 160146 | 323 | 0 | 80 | 3906 | 175 | 3906 | 16 | 3906 | 96 | 0 | 300 | 0 | 1511387.64 | 139900030.2 | 386.94 | 35816.7
29 | Vehari | Doulta Abad | Rural | 5588 | 402 | 120.6 | 673912.8 | 6 | 287.4 | 1927189.44 | 574.8 | 3854378.88 | 45 | 251460 | 74 | 413512 | 408 | 0 | 80 | 5588 | 175 | 5588 | 16 | 5588 | 96 | 0 | 300 | 0 | 2852562.24 | 258095191.2 | 510.48 | 46187.4
30 | Vehari | Nadir Wali | Rural | 5644 | 420 | 126 | 711144 | 16 | 310 | 2099568 | 620 | 4199136 | 15 | 84660 | 36 | 203184 | 436 | 0 | 80 | 5644 | 175 | 5644 | 16 | 0 | 96 | 0 | 300 | 0 | 2895372 | 266272632 | 513 | 47178
31 | Vehari | Zia Shaheed | Rural | 2004 | 134 | 40.2 | 80560.8 | 4 | 97.8 | 235189.44 | 195.6 | 470378.88 | 22 | 44088 | 49 | 98196 | 138 | 0 | 80 | 2004 | 175 | 2004 | 16 | 2004 | 96 | 0 | 300 | 0 | 359838.24 | 34356175.2 | 179.56 | 17143.8
32 | Burewala | Kamand | Rural | 3983 | 454 | 136.2 | 542484.6 | 34 | 351.8 | 1681463.28 | 703.6 | 3362926.56 | 34 | 135422 | 62 | 246946 | 488 | 0 | 80 | 3983 | 175 | 3983 | 16 | 3983 | 96 | 0 | 300 | 0 | 2359369.88 | 218219807.4 | 592.36 | 54787.8
33 | Burewala | S-S-Din | Rural | 4111 | 458 | 137.4 | 564851.4 | 22 | 342.6 | 1690114.32 | 685.2 | 3380228.64 | 20 | 82220 | 37 | 152107 | 480 | 0 | 80 | 4111 | 175 | 4111 | 16 | 4111 | 96 | 0 | 300 | 0 | 2337185.72 | 213634692.6 | 568.52 | 51966.6
34 | Burewala | Baba Fareed | Rural | 4255 | 500 | 150 | 638250 | 20 | 370 | 1889220 | 740 | 3778440 | 16 | 68080 | 32 | 136160 | 520 | 0 | 80 | 4255 | 175 | 4255 | 16 | 0 | 96 | 0 | 300 | 0 | 2595550 | 236790750 | 610 | 55650
35 | Burewala | Sultan | Rural | 5590 | 260 | 78 | 436020 | 6 | 188 | 1261104 | 376 | 2522208 | 9 | 50310 | 42 | 234780 | 266 | 0 | 80 | 5590 | 175 | 5590 | 16 | 0 | 96 | 0 | 300 | 0 | 1747434 | 166727340 | 312.6 | 29826
36 | Burewala | Zafar Shaheed | Rural | 3069 | 201 | 60.3 | 185060.7 | 4 | 144.7 | 532901.16 | 289.4 | 1065802.32 | 12 | 36828 | 33 | 101277 | 205 | 0 | 80 | 3069 | 175 | 3069 | 16 | 0 | 96 | 0 | 300 | 0 | 754789.86 | 70579941.3 | 245.94 | 22997.7
37 | Burewala | Al-Rehman | Rural | 3984 | 311 | 93.3 | 371707.2 | 8 | 225.7 | 1079026.56 | 451.4 | 2158053.12 | 16 | 63744 | 29 | 115536 | 319 | 0 | 80 | 3984 | 175 | 3984 | 16 | 0 | 96 | 0 | 300 | 0 | 1514477.76 | 137530468.8 | 380.14 | 34520.7
38 | Burewala | Jaman Shah | Rural | 3032 | 204 | 61.2 | 185558.4 | 21 | 163.8 | 595969.92 | 327.6 | 1191939.84 | 14 | 42448 | 27 | 81864 | 225 | 0 | 80 | 3032 | 175 | 3032 | 16 | 0 | 96 | 0 | 300 | 0 | 823976.32 | 76984905.6 | 271.76 | 25390.8
39 | Burewala | Dallan Bunglow | Rural | 4855 | 605 | 181.5 | 881182.5 | 24 | 447.5 | 2607135 | 895 | 5214270 | 42 | 203910 | 71 | 344705 | 629 | 0 | 80 | 4855 | 175 | 4855 | 16 | 4855 | 96 | 0 | 300 | 0 | 3692227.5 | 336182047.5 | 760.5 | 69244.5
40 | Burewala | Dewan Sahib | Rural | 6172 | 427 | 128.1 | 790633.2 | 35 | 333.9 | 2472996.96 | 667.8 | 4945993.92 | 75 | 462900 | 88 | 543136 | 462 | 0 | 80 | 6172 | 175 | 6172 | 16 | 6172 | 96 | 0 | 300 | 0 | 3726530.16 | 331719694.8 | 603.78 | 53745.9
41 | Burewala | Fateh Shah | Rural | 4650 | 414 | 124.2 | 577530 | 21 | 310.8 | 1734264 | 621.6 | 3468528 | 60 | 279000 | 65 | 302250 | 435 | 0 | 80 | 4650 | 175 | 4650 | 16 | 4650 | 96 | 0 | 300 | 0 | 2590794 | 227979270 | 557.16 | 49027.8
42 | Burewala | Tufail Shaheed | Rural | 3244 | 774 | 232.2 | 753256.8 | 35 | 576.8 | 2245367.04 | 1153.6 | 4490734.08 | 102 | 330888 | 240 | 778560 | 809 | 0 | 80 | 3244 | 175 | 3244 | 16 | 3244 | 96 | 3244 | 300 | 0 | 3329511.84 | 318417415.2 | 1026.36 | 98155.8
43 | Burewala | Lahore Road | Rural | 4233 | 44 | 13.2 | 55875.6 | 5 | 35.8 | 181849.68 | 71.6 | 363699.36 | 3 | 12699 | 4 | 16932 | 49 | 0 | 80 | 0 | 175 | 0 | 16 | 4233 | 96 | 0 | 300 | 0 | 250424.28 | 23005508.4 | 59.16 | 5434.8
44 | Burewala | Shah Faisal | Rural | 5060 | 378 | 113.4 | 573804 | 44 | 308.6 | 1873819.2 | 617.2 | 3747638.4 | 82 | 414920 | 162 | 819720 | 422 | 0 | 80 | 5060 | 175 | 5060 | 16 | 5060 | 96 | 5060 | 300 | 0 | 2862543.2 | 275762916 | 565.72 | 54498.6
45 | Burewala | Khairwala | Rural | 4467 | 196 | 58.8 | 262659.6 | 35 | 172.2 | 923060.88 | 344.4 | 1846121.76 | 64 | 285888 | 73 | 326091 | 231 | 0 | 80 | 4467 | 175 | 4467 | 16 | 4467 | 96 | 0 | 300 | 0 | 1471608.48 | 131120744.4 | 329.44 | 29353.2
46 | Burewala | Ghous Pak | Rural | 5735 | 176 | 52.8 | 302808 | 10 | 133.2 | 916682.4 | 266.4 | 1833364.8 | 232 | 1330520 | 88 | 504680 | 186 | 0 | 80 | 5735 | 175 | 5735 | 16 | 5735 | 96 | 0 | 300 | 0 | 2550010.4 | 141191112 | 444.64 | 24619.2
47 | Burewala | Sabir Raza Shaheed | Rural | 3408 | 181 | 54.3 | 185054.4 | 16 | 142.7 | 583585.92 | 285.4 | 1167171.84 | 48 | 163584 | 85 | 289680 | 197 | 0 | 80 | 3408 | 175 | 3408 | 16 | 3408 | 96 | 0 | 300 | 0 | 932224.32 | 87966273.6 | 273.54 | 25811.7
48 | Burewala | Gaggo | Rural | 6222 | 444 | 133.2 | 828770.4 | 13 | 323.8 | 2417620.32 | 647.6 | 4835240.64 | 46 | 286212 | 62 | 385764 | 457 | 0 | 80 | 6222 | 175 | 6222 | 16 | 6222 | 96 | 0 | 300 | 0 | 3532602.72 | 315746589.6 | 567.76 | 50746.8
49 | Burewala | Sheikh Fazal | Rural | 5949 | 396 | 118.8 | 706741.2 | 0 | 277.2 | 1978875.36 | 554.4 | 3957750.72 | 6 | 35694 | 30 | 178470 | 396 | 0 | 80 | 5949 | 175 | 5949 | 16 | 0 | 96 | 0 | 300 | 0 | 2721310.56 | 250293466.8 | 457.44 | 42073.2
50 | Burewala | Rasool Pur | Rural | 6913 | 536 | 160.8 | 1111610.4 | 6 | 381.2 | 3162282.72 | 762.4 | 6324565.44 | 14 | 96782 | 47 | 324911 | 542 | 0 | 80 | 6913 | 175 | 6913 | 16 | 0 | 96 | 0 | 300 | 0 | 4370675.12 | 402303417.6 | 632.24 | 58195.2
51 | Burewala | Farid | Rural | 4517 | 464 | 139.2 | 628766.4 | 3 | 327.8 | 1776807.12 | 655.6 | 3553614.24 | 31 | 140027 | 135 | 609795 | 467 | 0 | 80 | 4517 | 175 | 4517 | 16 | 4517 | 96 | 4517 | 300 | 0 | 2545600.52 | 251690853.6 | 563.56 | 55720.8
52 | Burewala | Saleem Shaheed | Rural | 2213 | 30 | 9 | 19917 | 2 | 23 | 61078.8 | 46 | 122157.6 | 1 | 2213 | 1 | 2213 | 32 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 83208.8 | 7521987 | 37.6 | 3399
53 | Burewala | Arif Shah | Rural | 5455 | 267 | 80.1 | 436945.5 | 2 | 188.9 | 1236539.4 | 377.8 | 2473078.8 | 25 | 136375 | 56 | 305480 | 269 | 0 | 80 | 5455 | 175 | 5455 | 16 | 5455 | 96 | 0 | 300 | 0 | 1809859.9 | 168024364.5 | 331.78 | 30801.9
54 | Burewala | Machiwal | Rural | 7851 | 380 | 114 | 895014 | 25 | 291 | 2741569.2 | 582 | 5483138.4 | 47 | 368997 | 116 | 910716 | 405 | 0 | 80 | 7851 | 175 | 7851 | 16 | 7851 | 96 | 7851 | 300 | 0 | 4005580.2 | 386316306 | 510.2 | 49206
55 | Burewala | B&R | Rural | 4699 | 467 | 140.1 | 658329.9 | 11 | 337.9 | 1905350.52 | 675.8 | 3810701.04 | 225 | 1057275 | 82 | 385318 | 478 | 0 | 80 | 4699 | 175 | 4699 | 16 | 4699 | 96 | 0 | 300 | 0 | 3620955.42 | 253736132.1 | 770.58 | 53997.9
56 | Burewala | Zaheer Nagar | Rural | 5575 | 497 | 149.1 | 831232.5 | 32 | 379.9 | 2541531 | 759.8 | 5083062 | 55 | 306625 | 78 | 434850 | 529 | 0 | 80 | 5575 | 175 | 5575 | 16 | 5575 | 96 | 0 | 300 | 0 | 3679388.5 | 333568417.5 | 659.98 | 59832.9
57 | Burewala | M/Colony | Rural | 4493 | 414 | 124.2 | 558030.6 | 13 | 302.8 | 1632576.48 | 605.6 | 3265152.96 | 230 | 1033390 | 87 | 390891 | 427 | 0 | 80 | 4493 | 175 | 4493 | 16 | 4493 | 96 | 0 | 300 | 0 | 3223997.08 | 221036729.4 | 717.56 | 49195.8
58 | Burewala | Sahuka | Rural | 2722 | 323 | 96.9 | 263761.8 | 5 | 231.1 | 754865.04 | 462.2 | 1509730.08 | 43 | 117046 | 89 | 242258 | 328 | 0 | 80 | 2722 | 175 | 2722 | 16 | 2722 | 96 | 0 | 300 | 0 | 1135672.84 | 105910570.2 | 417.22 | 38909.1
59 | Burewala | Haji Sher | Rural | 5694 | 435 | 130.5 | 743067 | 9 | 313.5 | 2142082.8 | 627 | 4284165.6 | 46 | 261924 | 107 | 609258 | 444 | 0 | 80 | 5694 | 175 | 5694 | 16 | 5694 | 96 | 5694 | 300 | 0 | 3147073.8 | 295834617 | 552.7 | 51955.5
60 | Burewala | Saldera | Rural | 5312 | 725 | 217.5 | 1155360 | 10 | 517.5 | 3298752 | 1035 | 6597504 | 44 | 233728 | 94 | 499328 | 735 | 0 | 80 | 5312 | 175 | 5312 | 16 | 5312 | 96 | 0 | 300 | 0 | 4687840 | 429276000 | 882.5 | 80812.5
61 | Burewala | Umer Pur | Rural | 5659 | 367 | 110.1 | 623055.9 | 8 | 264.9 | 1798882.92 | 529.8 | 3597765.84 | 43 | 243337 | 85 | 481015 | 375 | 0 | 80 | 5659 | 175 | 5659 | 16 | 5659 | 96 | 0 | 300 | 0 | 2665275.82 | 246596018.1 | 470.98 | 43575.9
62 | Burewala | Al-Abbas | Rural | 5671 | 580 | 174 | 986754 | 8 | 414 | 2817352.8 | 828 | 5634705.6 | 49 | 277879 | 101 | 572771 | 588 | 0 | 80 | 5671 | 175 | 5671 | 16 | 5671 | 96 | 5671 | 300 | 0 | 4081985.8 | 375408858 | 719.8 | 66198
63 | Burewala | Jamlera | Rural | 4885 | 754 | 226.2 | 1104987 | 5 | 532.8 | 3123273.6 | 1065.6 | 6246547.2 | 650 | 3175250 | 713 | 3483005 | 759 | 0 | 80 | 4885 | 175 | 4885 | 16 | 4885 | 96 | 4885 | 300 | 0 | 7403510.6 | 587088093 | 1515.56 | 120181.8
64 | Burewala | Murad Ali | Rural | 2032 | 347 | 104.1 | 211531.2 | 6 | 248.9 | 606917.76 | 497.8 | 1213835.52 | 295 | 599440 | 335 | 680720 | 353 | 0 | 80 | 2032 | 175 | 2032 | 16 | 2032 | 96 | 2032 | 300 | 0 | 1417888.96 | 114307924.8 | 697.78 | 56253.9
65 | Burewala | Sarwar Shah | Rural | 2364 | 198 | 59.4 | 140421.6 | 4 | 142.6 | 404527.68 | 285.2 | 809055.36 | 348 | 822672 | 390 | 921960 | 202 | 0 | 80 | 2364 | 175 | 2364 | 16 | 2364 | 96 | 2364 | 300 | 0 | 1367621.28 | 104282186.4 | 578.52 | 44112.6
66 | Burewala | Sadat | Rural | 1675 | 661 | 198.3 | 332152.5 | 11 | 473.7 | 952137 | 947.4 | 1904274 | 932 | 1561100 | 645 | 1080375 | 672 | 0 | 80 | 1675 | 175 | 1675 | 16 | 1675 | 96 | 1675 | 300 | 0 | 2845389.5 | 180075397.5 | 1698.74 | 107507.7
67 | Burewala | Jodheka | Rural | 1614 | 363 | 108.9 | 175764.6 | 5 | 259.1 | 501824.88 | 518.2 | 1003649.76 | 194 | 313116 | 235 | 379290 | 368 | 0 | 80 | 1614 | 175 | 1614 | 16 | 1614 | 96 | 1614 | 300 | 0 | 990705.48 | 83503679.4 | 613.82 | 51737.1
68 | Mailsi | Syphon | Rural | 5610 | 794 | 238.2 | 1336302 | 48 | 603.8 | 4064781.6 | 1207.6 | 8129563.2 | 84 | 471240 | 125 | 701250 | 842 | 0 | 80 | 5610 | 175 | 5610 | 16 | 5610 | 96 | 5610 | 300 | 0 | 5872323.6 | 533857698 | 1046.76 | 95161.8
69 | Mailsi | Khan Pur | Rural | 4916 | 79 | 23.7 | 116509.2 | 1 | 56.3 | 332124.96 | 112.6 | 664249.92 | 41 | 201556 | 42 | 206472 | 80 | 0 | 80 | 4916 | 175 | 0 | 16 | 4916 | 96 | 0 | 300 | 0 | 650190.16 | 52592842.8 | 132.26 | 10698.3
70 | Mailsi | Alam Pur | Rural | 5843 | 561 | 168.3 | 983376.9 | 39 | 431.7 | 3026907.72 | 863.4 | 6053815.44 | 76 | 444068 | 113 | 660259 | 600 | 0 | 80 | 5843 | 175 | 5843 | 16 | 5843 | 96 | 5843 | 300 | 0 | 4454352.62 | 405794597.1 | 762.34 | 69449.7
71 | Mailsi | Sargana | Rural | 4903 | 599 | 179.7 | 881069.1 | 27 | 446.3 | 2625850.68 | 892.6 | 5251701.36 | 61 | 299083 | 99 | 485397 | 626 | 0 | 80 | 4903 | 175 | 4903 | 16 | 4903 | 96 | 4903 | 300 | 0 | 3806002.78 | 346869108.9 | 776.26 | 70746.3
72 | Mailsi | shair garh | Rural | 2963 | 468 | 140.4 | 416005.2 | 23 | 350.6 | 1246593.36 | 701.2 | 2493186.72 | 64 | 189632 | 101 | 299263 | 491 | 0 | 80 | 2963 | 175 | 2963 | 16 | 2963 | 96 | 2963 | 300 | 0 | 1852230.56 | 168794998.8 | 625.12 | 56967.6
73 | Mailsi | Karam Pur | Rural | 6504 | 415 | 124.5 | 809748 | 4 | 294.5 | 2298513.6 | 589 | 4597027.2 | 45 | 292680 | 113 | 734952 | 419 | 0 | 80 | 6504 | 175 | 6504 | 16 | 6504 | 96 | 6504 | 300 | 0 | 3400941.6 | 322347996 | 522.9 | 49561.5
74 | Mailsi | Aftab | Rural | 2446 | 520 | 156 | 381576 | 7 | 371 | 1088959.2 | 742 | 2177918.4 | 99 | 242154 | 111 | 271506 | 527 | 0 | 80 | 2446 | 175 | 2446 | 16 | 2446 | 96 | 2446 | 300 | 0 | 1712689.2 | 148110192 | 700.2 | 60552
75 | Mailsi | Irshad Khan | Rural | 7008 | 585 | 175.5 | 1229904 | 26 | 435.5 | 3662380.8 | 871 | 7324761.6 | 92 | 644736 | 124 | 868992 | 611 | 0 | 80 | 7008 | 175 | 7008 | 16 | 7008 | 96 | 7008 | 300 | 0 | 5537020.8 | 495314928 | 790.1 | 70678.5
76 | Mailsi | Jallah | Rural | 6629 | 530 | 159 | 1054011 | 25 | 396 | 3150100.8 | 792 | 6300201.6 | 105 | 696045 | 202 | 1339058 | 555 | 0 | 80 | 6629 | 175 | 6629 | 16 | 6629 | 96 | 6629 | 300 | 0 | 4900156.8 | 461517609 | 739.2 | 69621
77 | Mailsi | Shakar Gunj | Rural | 6490 | 489 | 146.7 | 952083 | 21 | 363.3 | 2829380.4 | 726.6 | 5658760.8 | 106 | 687940 | 174 | 1129260 | 510 | 0 | 80 | 6490 | 175 | 6490 | 16 | 6490 | 96 | 6490 | 300 | 0 | 4469403.4 | 410137497 | 688.66 | 63195.3
78 | Mailsi | Kikri | Rural | 6728 | 518 | 155.4 | 1045531.2 | 43 | 405.6 | 3274652.16 | 811.2 | 6549304.32 | 103 | 692984 | 181 | 1217768 | 561 | 0 | 80 | 6728 | 175 | 6728 | 16 | 6728 | 96 | 6728 | 300 | 0 | 5013167.36 | 469160932.8 | 745.12 | 69732.6
79 | Mailsi | Niaz Pur | Rural | 6305 | 631 | 189.3 | 1193536.5 | 48 | 489.7 | 3705070.2 | 979.4 | 7410140.4 | 101 | 636805 | 142 | 895310 | 679 | 0 | 80 | 6305 | 175 | 6305 | 16 | 6305 | 96 | 6305 | 300 | 0 | 5535411.7 | 501907633.5 | 877.94 | 79604.7
80 | Mailsi | Zia Khan | Rural | 5708 | 413 | 123.9 | 707221.2 | 23 | 312.1 | 2137760.16 | 624.2 | 4275520.32 | 193 | 1101644 | 124 | 707792 | 436 | 0 | 80 | 5708 | 175 | 5708 | 16 | 5708 | 96 | 5708 | 300 | 0 | 3946625.36 | 301120402.8 | 691.42 | 52754.1
81 | Mailsi | Duniya Pur | Rural | 4744 | 321 | 96.3 | 456847.2 | 27 | 251.7 | 1432877.76 | 503.4 | 2865755.52 | 85 | 403240 | 120 | 569280 | 348 | 0 | 80 | 4744 | 175 | 4744 | 16 | 4744 | 96 | 4744 | 300 | 0 | 2292964.96 | 207472672.8 | 483.34 | 43733.7
82 | Mailsi | TSP-2 | Rural | 5081 | 251 | 75.3 | 382599.3 | 23 | 198.7 | 1211513.64 | 397.4 | 2423027.28 | 116 | 589396 | 268 | 1361708 | 274 | 0 | 80 | 5081 | 175 | 5081 | 16 | 5081 | 96 | 5081 | 300 | 0 | 2183508.94 | 228231914.7 | 429.74 | 44918.7
83 | Mailsi | TSP-1 | Rural | 11489 | 404 | 121.2 | 1392466.8 | 35 | 317.8 | 4381445.04 | 635.6 | 8762890.08 | 158 | 1815262 | 241 | 2768849 | 439 | 0 | 80 | 11489 | 175 | 11489 | 16 | 11489 | 96 | 11489 | 300 | 0 | 7589173.84 | 696081745.2 | 660.56 | 60586.8
84 | Mailsi | Chak Shahna | Rural | 6109 | 442 | 132.6 | 810053.4 | 17 | 326.4 | 2392773.12 | 652.8 | 4785546.24 | 87 | 531483 | 124 | 757516 | 459 | 0 | 80 | 6109 | 175 | 6109 | 16 | 6109 | 96 | 6109 | 300 | 0 | 3734309.52 | 335013894.6 | 611.28 | 54839.4
85 | Mailsi | G.More | Rural | 5903 | 436 | 130.8 | 772112.4 | 21 | 326.2 | 2310670.32 | 652.4 | 4621340.64 | 163 | 962189 | 422 | 2491066 | 457 | 0 | 80 | 5903 | 175 | 5903 | 16 | 5903 | 96 | 5903 | 300 | 0 | 4044971.72 | 429060735.6 | 685.24 | 72685.2
86 | Mailsi | Chakliar | Rural | 8024 | 158 | 47.4 | 380337.6 | 11 | 121.6 | 1170862.08 | 243.2 | 2341724.16 | 75 | 601800 | 118 | 946832 | 169 | 0 | 80 | 8024 | 175 | 8024 | 16 | 8024 | 96 | 8024 | 300 | 0 | 2152999.68 | 198454382.4 | 268.32 | 24732.6
87 | Mailsi | Factory | Rural | 2254 | 228 | 68.4 | 154173.6 | 15 | 174.6 | 472258.08 | 349.2 | 944516.16 | 109 | 245686 | 181 | 407974 | 243 | 0 | 80 | 2254 | 175 | 2254 | 16 | 2254 | 96 | 2254 | 300 | 0 | 872117.68 | 81611930.4 | 386.92 | 36207.6
88 | Mailsi | Safeer Nagar | Rural | 3509 | 182 | 54.6 | 191591.4 | 19 | 146.4 | 616461.12 | 292.8 | 1232922.24 | 101 | 354409 | 136 | 477224 | 201 | 0 | 80 | 3509 | 175 | 3509 | 16 | 3509 | 96 | 3509 | 300 | 0 | 1162461.52 | 103183548.6 | 331.28 | 29405.4
89 | Mailsi | SPJ | Rural | 3802 | 456 | 136.8 | 520113.6 | 19 | 338.2 | 1543003.68 | 676.4 | 3086007.36 | 75 | 285150 | 118 | 448636 | 475 | 0 | 80 | 3802 | 175 | 3802 | 16 | 3802 | 96 | 3802 | 300 | 0 | 2348267.28 | 213638942.4 | 617.64 | 56191.2
90 | Mailsi | Alam Dar | Rural | 2072 | 311 | 93.3 | 193317.6 | 13 | 230.7 | 573612.48 | 461.4 | 1147224.96 | 83 | 171976 | 85 | 176120 | 324 | 0 | 80 | 2072 | 175 | 2072 | 16 | 2072 | 96 | 0 | 300 | 0 | 938906.08 | 79980650.4 | 453.14 | 38600.7
91 | Mailsi | Rashid Minhas | Rural | 4873 | 388 | 116.4 | 567217.2 | 18 | 289.6 | 1693464.96 | 579.2 | 3386929.92 | 349 | 1700677 | 258 | 1257234 | 406 | 0 | 80 | 4873 | 175 | 4873 | 16 | 4873 | 96 | 4873 | 300 | 0 | 3961359.16 | 280351486.8 | 812.92 | 57531.6
92 | Mailsi | Dokota | Rural | 5603 | 320 | 96 | 537888 | 20 | 244 | 1640558.4 | 488 | 3281116.8 | 123 | 689169 | 163 | 913289 | 340 | 0 | 80 | 5603 | 175 | 5603 | 16 | 5603 | 96 | 5603 | 300 | 0 | 2867615.4 | 253278012 | 511.8 | 45204
93 | Mailsi | Shair Mohammad | Rural | 4758 | 332 | 99.6 | 473896.8 | 18 | 250.4 | 1429683.84 | 500.8 | 2859367.68 | 98 | 466284 | 106 | 504348 | 350 | 0 | 80 | 4758 | 175 | 4758 | 16 | 4758 | 96 | 4758 | 300 | 0 | 2369864.64 | 203244631.2 | 498.08 | 42716.4
94 | Mailsi | Gazi Abbas | Rural | 4242 | 346 | 103.8 | 440319.6 | 13 | 255.2 | 1299070.08 | 510.4 | 2598140.16 | 101 | 428442 | 109 | 462378 | 359 | 0 | 80 | 4242 | 175 | 4242 | 16 | 4242 | 96 | 4242 | 300 | 0 | 2167831.68 | 184952048.4 | 511.04 | 43600.2
95 | Mailsi | Fida Shahaeed | Rural | 2390 | 231 | 69.3 | 165627 | 20 | 181.7 | 521115.6 | 363.4 | 1042231.2 | 66 | 157740 | 76 | 181640 | 251 | 0 | 80 | 2390 | 175 | 2390 | 16 | 2390 | 96 | 0 | 300 | 0 | 844482.6 | 73929153 | 353.34 | 30932.7
96 | Mailsi | Shair Shah | Rural | 5459 | 228 | 68.4 | 373395.6 | 17 | 176.6 | 1156871.28 | 353.2 | 2313742.56 | 94 | 513146 | 56 | 305704 | 245 | 0 | 80 | 5459 | 175 | 5459 | 16 | 5459 | 96 | 0 | 300 | 0 | 2043412.88 | 158286980.4 | 374.32 | 28995.6
97 | Mailsi | Mitroo | Rural | 5319 | 364 | 109.2 | 580834.8 | 20 | 274.8 | 1753993.44 | 549.6 | 3507986.88 | 148 | 787212 | 269 | 1430811 | 384 | 0 | 80 | 5319 | 175 | 5319 | 16 | 5319 | 96 | 5319 | 300 | 0 | 3122040.24 | 298070377.2 | 586.96 | 56038.8
|  | TOTAL |  | 442791 | 29453 | 9963 | 51335287.8 | 1299 | 24774 | 153773925.84 | 49548 | 307547851.68 | 6913 | 33515197 | 11097 | 47062260 | 34737 | 0 | 80 | 436345 | 175 | 431429 | 16 | 390701 | 96 | 183089 | 300 | 0 | 238624410.64 | 21430612564.2 | 538.9098 | 48398.9344

## 400-220 (Rural) B-Pur
Statement of 400/220 V MEPCO Consumers For 2020-21
Bahawal Pur Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | City Bahawalpur | Jhangi Wala | Rural | 7747 | 276 | 82.8 | 641451.6 | 17 | 210.2 | 1954103.28 | 420.4 | 3908206.56 | 15 | 116205 | 66 | 511302 | 293 | 0 | 80 | 7747 | 175 | 7747 | 16 | 0 | 96 | 0 | 300 | 0 | 2711759.88 | 267094868.4 | 350.04 | 34477.2
2 | City Bahawalpur | Azadi | Rural | 1643 | 255 | 76.5 | 125689.5 | 16 | 194.5 | 383476.2 | 389 | 766952.4 | 305 | 501115 | 336 | 552048 | 271 | 0 | 80 | 1643 | 175 | 1643 | 16 | 1643 | 96 | 1643 | 300 | 0 | 1010280.7 | 79517092.5 | 614.9 | 48397.5
3 | City Bahawalpur | Dera Bakkha | Rural | 4569 | 135 | 40.5 | 185044.5 | 11 | 105.5 | 578435.4 | 211 | 1156870.8 | 14 | 63966 | 76 | 347244 | 146 | 0 | 80 | 4569 | 175 | 4569 | 16 | 0 | 96 | 0 | 300 | 0 | 827445.9 | 90802021.5 | 181.1 | 19873.5
4 | City Bahawalpur | Nawab Pur | Rural | 3964 | 119 | 35.7 | 141514.8 | 16 | 99.3 | 472350.24 | 198.6 | 944700.48 | 9 | 35676 | 39 | 154596 | 135 | 0 | 80 | 3964 | 175 | 3964 | 16 | 0 | 96 | 0 | 300 | 0 | 649541.04 | 66382333.2 | 163.86 | 16746.3
5 | City Bahawalpur | Azhar | Rural | 1221 | 37 | 11.1 | 13553.1 | 1 | 26.9 | 39413.88 | 53.8 | 78827.76 | 1 | 1221 | 4 | 4884 | 38 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 54187.98 | 5063364.9 | 44.38 | 4146.9
6 | City Bahawalpur | National Park | Rural | 3082 | 426 | 127.8 | 393879.6 | 67 | 365.2 | 1350655.68 | 730.4 | 2701311.36 | 6 | 18492 | 25 | 77050 | 493 | 0 | 80 | 3082 | 175 | 3082 | 16 | 0 | 96 | 0 | 300 | 0 | 1763027.28 | 167883320.4 | 572.04 | 54472.2
7 | City Bahawalpur | Abbas Nagar | Rural | 3740 | 350 | 105 | 392700 | 59 | 304 | 1364352 | 608 | 2728704 | 8 | 29920 | 33 | 123420 | 409 | 0 | 80 | 3740 | 175 | 3740 | 16 | 0 | 96 | 0 | 300 | 0 | 1786972 | 172305540 | 477.8 | 46071
8 | City Bahawalpur | Pully Islamabad | Rural | 4379 | 252 | 75.6 | 331052.4 | 60 | 236.4 | 1242234.72 | 472.8 | 2484469.44 | 6 | 26274 | 26 | 113854 | 312 | 0 | 80 | 4379 | 175 | 4379 | 16 | 0 | 96 | 0 | 300 | 0 | 1599561.12 | 156892563.6 | 365.28 | 35828.4
9 | City Bahawalpur | Gudden | Rural | 619 | 124 | 37.2 | 23026.8 | 58 | 144.8 | 107557.44 | 289.6 | 215114.88 | 8 | 4952 | 35 | 21665 | 182 | 0 | 80 | 619 | 175 | 619 | 16 | 0 | 96 | 0 | 300 | 0 | 135536.24 | 14275873.2 | 218.96 | 23062.8
10 | City Bahawalpur | Jumman Shaheed | Rural | 1349 | 252 | 75.6 | 101984.4 | 60 | 236.4 | 382684.32 | 472.8 | 765368.64 | 6 | 8094 | 26 | 35074 | 312 | 0 | 80 | 1349 | 175 | 1349 | 16 | 0 | 96 | 0 | 300 | 0 | 492762.72 | 48332511.6 | 365.28 | 35828.4
11 | City Bahawalpur | Cholistan | Rural | 5155 | 190 | 57 | 293835 | 66 | 199 | 1231014 | 398 | 2462028 | 3 | 15465 | 14 | 72170 | 256 | 0 | 80 | 5155 | 175 | 5155 | 16 | 0 | 96 | 0 | 300 | 0 | 1540314 | 152933385 | 298.8 | 29667
12 | City Bahawalpur | Kud Wala | Rural | 2128 | 129 | 38.7 | 82353.6 | 37 | 127.3 | 325073.28 | 254.6 | 650146.56 | 3 | 6384 | 15 | 31920 | 166 | 0 | 80 | 2128 | 175 | 2128 | 16 | 0 | 96 | 0 | 300 | 0 | 413810.88 | 41171054.4 | 194.46 | 19347.3
13 | City Bahawalpur | 42-db | Rural | 5400 | 110 | 33 | 178200 | 51 | 128 | 829440 | 256 | 1658880 | 4 | 21600 | 17 | 91800 | 161 | 0 | 80 | 5400 | 175 | 5400 | 16 | 0 | 96 | 0 | 300 | 0 | 1029240 | 105575400 | 190.6 | 19551
14 | City Bahawalpur | Channan Peer | Rural | 5491 | 161 | 48.3 | 265215.3 | 163 | 275.7 | 1816642.44 | 551.4 | 3633284.88 | 3 | 16473 | 12 | 65892 | 324 | 0 | 80 | 5491 | 175 | 5491 | 16 | 0 | 96 | 0 | 300 | 0 | 2098330.74 | 222746258.7 | 382.14 | 40565.7
15 | City Bahawalpur | Tail Wala | Rural | 5069 | 172 | 51.6 | 261560.4 | 57 | 177.4 | 1079088.72 | 354.8 | 2158177.44 | 304 | 1540976 | 315 | 1596735 | 229 | 0 | 80 | 5069 | 175 | 5069 | 16 | 5069 | 96 | 5069 | 300 | 0 | 2881625.12 | 226079427.6 | 568.48 | 44600.4
16 | City Bahawalpur | Amin Shaheed | Rural | 7465 | 229 | 68.7 | 512845.5 | 77 | 237.3 | 2125733.4 | 474.6 | 4251466.8 | 4 | 29860 | 15 | 111975 | 306 | 0 | 80 | 7465 | 175 | 7465 | 16 | 0 | 96 | 0 | 300 | 0 | 2668438.9 | 263345044.5 | 357.46 | 35277.3
17 | City Bahawalpur | Dunyapur | Rural | 2764 | 134 | 40.2 | 111112.8 | 66 | 159.8 | 530024.64 | 319.6 | 1060049.28 | 3 | 8292 | 15 | 41460 | 200 | 0 | 80 | 2764 | 175 | 2764 | 16 | 0 | 96 | 0 | 300 | 0 | 649429.44 | 66423895.2 | 234.96 | 24031.8
18 | City Bahawalpur | Rohi | Rural | 7600 | 166 | 49.8 | 378480 | 37 | 153.2 | 1397184 | 306.4 | 2794368 | 3 | 22800 | 12 | 91200 | 203 | 0 | 80 | 7600 | 175 | 7600 | 16 | 0 | 96 | 0 | 300 | 0 | 1798464 | 174269520 | 236.64 | 22930.2
19 | Lodhran | Dhannot | Rural | 9157 | 131 | 39.3 | 359870.1 | 113 | 204.7 | 2249325.48 | 409.4 | 4498650.96 | 21 | 192297 | 109 | 998113 | 243 | 1 | 80 | 9157 | 175 | 9157 | 16 | 9157 | 96 | 9157 | 300 | 0 | 2801492.58 | 330885447.9 | 305.94 | 36134.7
20 | Lodhran | Havaili Nasir Khan | Rural | 2305 | 276 | 82.8 | 190854 | 121 | 314.2 | 869077.2 | 628.4 | 1738154.4 | 11 | 25355 | 40 | 92200 | 396 | 1 | 80 | 2305 | 175 | 2305 | 16 | 0 | 96 | 0 | 300 | 0 | 1085286.2 | 110393826 | 470.84 | 47893.2
21 | Lodhran | Jhok Haq Nawaz | Rural | 3018 | 235 | 70.5 | 212769 | 56 | 220.5 | 798562.8 | 441 | 1597125.6 | 10 | 30180 | 40 | 120720 | 290 | 1 | 80 | 3018 | 175 | 3018 | 16 | 0 | 96 | 0 | 300 | 0 | 1041511.8 | 103709043 | 345.1 | 34363.5
22 | Lodhran | Layal Pur | Rural | 3941 | 492 | 147.6 | 581691.6 | 65 | 409.4 | 1936134.48 | 818.8 | 3872268.96 | 18 | 70938 | 66 | 260106 | 556 | 1 | 80 | 3941 | 175 | 3941 | 16 | 3941 | 96 | 0 | 300 | 0 | 2588764.08 | 249687572.4 | 656.88 | 63356.4
23 | Lodhran | Sarfaraz Shaheed | Rural | 2537 | 172 | 51.6 | 130909.2 | 25 | 145.4 | 442655.76 | 290.8 | 885311.52 |  | 0 | 8 | 20296 | 197 |  | 80 | 2537 | 175 | 2537 | 16 | 0 | 96 | 0 | 300 | 0 | 573564.96 | 54729178.8 | 226.08 | 21572.4
24 | Lodhran | Raja Pur | Rural | 4421 | 308 | 92.4 | 408500.4 | 107 | 322.6 | 1711457.52 | 645.2 | 3422915.04 | 18 | 79578 | 86 | 380206 | 414 | 1 | 80 | 4421 | 175 | 4421 | 16 | 4421 | 96 | 0 | 300 | 0 | 2199535.92 | 229412763.6 | 497.52 | 51891.6
25 | Lodhran | Mustafa Shaheed | Rural | 1898 | 112 | 33.6 | 63772.8 | 19 | 97.4 | 221838.24 | 194.8 | 443676.48 |  | 0 | 7 | 13286 | 131 |  | 80 | 1898 | 175 | 1898 | 16 | 0 | 96 | 0 | 300 | 0 | 285611.04 | 27609067.2 | 150.48 | 14546.4
26 | Lodhran | Rawani | Rural | 3402 | 192 | 57.6 | 195955.2 | 103 | 237.4 | 969161.76 | 474.8 | 1938323.52 | 64 | 217728 | 87 | 295974 | 294 | 1 | 80 | 3402 | 175 | 3402 | 16 | 3402 | 96 | 0 | 300 | 0 | 1382844.96 | 134645716.8 | 406.48 | 39578.4
27 | Lodhran | Sardar Pur | Rural | 3949 | 136 | 40.8 | 161119.2 | 107 | 202.2 | 958185.36 | 404.4 | 1916370.72 | 7 | 27643 | 22 | 86878 | 242 | 1 | 80 | 3949 | 175 | 3949 | 16 | 0 | 96 | 0 | 300 | 0 | 1146947.56 | 120678280.8 | 290.44 | 30559.2
28 | Lodhran | Sardar Pur 2 | Rural | 2098 | 25 | 7.5 | 15735 | 67 | 84.5 | 212737.2 | 169 | 425474.4 | 9 | 18882 | 33 | 69234 | 91 | 1 | 80 | 2098 | 175 | 2098 | 16 | 0 | 96 | 0 | 300 | 0 | 247354.2 | 29729709 | 117.9 | 14170.5
29 | Lodhran | Sher Awan | Rural | 3789 | 216 | 64.8 | 245527.2 | 92 | 243.2 | 1105781.76 | 486.4 | 2211563.52 | 5 | 18945 | 18 | 68202 | 307 | 1 | 80 | 3789 | 175 | 3789 | 16 | 0 | 96 | 0 | 300 | 0 | 1370253.96 | 137522512.8 | 361.64 | 36295.2
30 | Lodhran | 12-mpr | Rural | 1219 | 183 | 54.9 | 66923.1 | 24 | 152.1 | 222491.88 | 304.2 | 444983.76 | 7 | 8533 | 32 | 39008 | 207 | 0 | 80 | 1219 | 175 | 1219 | 16 | 0 | 96 | 0 | 300 | 0 | 297947.98 | 29240274.9 | 244.42 | 23987.1
31 | Lodhran | 53 M | Rural | 1100 | 200 | 60 | 66000 | 25 | 165 | 217800 | 330 | 435600 | 10 | 11000 | 79 | 86900 | 224 | 1 | 80 | 1100 | 175 | 1100 | 16 | 0 | 96 | 0 | 300 | 0 | 294800 | 31548000 | 268 | 28680
32 | Lodhran | Ali Tareen | Rural | 3623 | 218 | 65.4 | 236944.2 | 53 | 205.6 | 893866.56 | 411.2 | 1787733.12 | 9 | 32607 | 33 | 119559 | 270 | 1 | 80 | 3623 | 175 | 3623 | 16 | 0 | 96 | 0 | 300 | 0 | 1163417.76 | 115148359.8 | 321.12 | 31782.6
33 | Lodhran | City Galay Wal | Rural | 5774 | 389 | 116.7 | 673825.8 | 18 | 290.3 | 2011430.64 | 580.6 | 4022861.28 | 7 | 40418 | 32 | 184768 | 407 | 0 | 80 | 5774 | 175 | 5774 | 16 | 0 | 96 | 0 | 300 | 0 | 2725674.44 | 254479234.2 | 472.06 | 44073.3
34 | Lodhran | Jallah | Rural | 6859 | 152 | 45.6 | 312770.4 | 17 | 123.4 | 1015680.72 | 246.8 | 2031361.44 |  | 0 | 6 | 41154 | 169 |  | 80 | 6859 | 175 | 6859 | 16 | 0 | 96 | 0 | 300 | 0 | 1328451.12 | 125289237.6 | 193.68 | 18266.4
35 | Lodhran | Lutf Pur | Rural | 1622 | 156 | 46.8 | 75909.6 | 16 | 125.2 | 243689.28 | 250.4 | 487378.56 | 8 | 12976 | 30 | 48660 | 172 | 0 | 80 | 1622 | 175 | 1622 | 16 | 0 | 96 | 0 | 300 | 0 | 332574.88 | 32390042.4 | 205.04 | 19969.2
36 | Lodhran | Mian Pur | Rural | 2198 | 150 | 45 | 98910 | 17 | 122 | 321787.2 | 244 | 643574.4 | 18 | 39564 | 21 | 46158 | 167 | 0 | 80 | 2198 | 175 | 2198 | 16 | 2198 | 96 | 0 | 300 | 0 | 460261.2 | 41680674 | 209.4 | 18963
37 | Lodhran | Noori Lal | Rural | 1692 | 123 | 36.9 | 62434.8 | 59 | 145.1 | 294611.04 | 290.2 | 589222.08 | 5 | 8460 | 25 | 42300 | 182 | 0 | 80 | 1692 | 175 | 1692 | 16 | 0 | 96 | 0 | 300 | 0 | 365505.84 | 38078629.2 | 216.02 | 22505.1
38 | Lodhran | Rasool Pur | Rural | 2980 | 262 | 78.6 | 234228 | 18 | 201.4 | 720206.4 | 402.8 | 1440412.8 | 9 | 26820 | 43 | 128140 | 280 | 0 | 80 | 2980 | 175 | 2980 | 16 | 0 | 96 | 0 | 300 | 0 | 981254.4 | 94815852 | 329.28 | 31817.4
39 | Lodhran | Satluj | Rural | 2309 | 437 | 131.1 | 302709.9 | 100 | 405.9 | 1124667.72 | 811.8 | 2249335.44 | 14 | 32326 | 51.1 | 117989.9 | 536 | 1 | 80 | 2309 | 175 | 2309 | 16 | 0 | 96 | 0 | 300 | 0 | 1459703.62 | 142947650.1 | 632.18 | 61908.9
40 | Lodhran | Adam Wahan | Rural | 7619 | 688 | 206.4 | 1572561.6 | 118 | 599.6 | 5482022.88 | 1199.2 | 10964045.76 | 10 | 76190 | 46.3 | 352759.7 | 805 | 1 | 80 | 7619 | 175 | 7619 | 16 | 0 | 96 | 0 | 300 | 0 | 7130774.48 | 683726012.4 | 935.92 | 89739.6
41 | Lodhran | Galay Wala | Rural | 6223 | 280 | 84 | 522732 | 80 | 276 | 2061057.6 | 552 | 4122115.2 | 12 | 74676 | 48.45 | 301504.35 | 359 | 1 | 80 | 6223 | 175 | 6223 | 16 | 0 | 96 | 0 | 300 | 0 | 2658465.6 | 266985369 | 427.2 | 42903
42 | Lodhran | Gogran | Rural | 2796 | 309 | 92.7 | 259189.2 | 59 | 275.3 | 923686.56 | 550.6 | 1847373.12 | 7 | 19572 | 24 | 67104 | 367 | 1 | 80 | 2796 | 175 | 2796 | 16 | 0 | 96 | 0 | 300 | 0 | 1202447.76 | 115646194.8 | 430.06 | 41361.3
43 | Lodhran | Hukam Din | Rural | 2851 | 416 | 124.8 | 355804.8 | 92 | 383.2 | 1311003.84 | 766.4 | 2622007.68 | 6 | 17106 | 27 | 76977 | 508 | 0 | 80 | 2851 | 175 | 2851 | 16 | 0 | 96 | 0 | 300 | 0 | 1683914.64 | 163006495.2 | 590.64 | 57175.2
44 | Lodhran | Lal Kamal | Rural | 5377 | 447 | 134.1 | 721055.7 | 112 | 424.9 | 2741624.76 | 849.8 | 5483249.52 | 9 | 48393 | 35.1 | 188732.7 | 558 | 1 | 80 | 5377 | 175 | 5377 | 16 | 0 | 96 | 0 | 300 | 0 | 3511073.46 | 342482100.3 | 652.98 | 63693.9
45 | Lodhran | Saudullah Pur | Rural | 2136 | 407 | 122.1 | 260805.6 | 96 | 380.9 | 976322.88 | 761.8 | 1952645.76 | 7 | 14952 | 28.2 | 60235.2 | 503 | 0 | 80 | 2136 | 175 | 2136 | 16 | 0 | 96 | 0 | 300 | 0 | 1252080.48 | 121555274.4 | 586.18 | 56907.9
46 | Lodhran | Shahidan Wala | Rural | 4495 | 446 | 133.8 | 601431 | 78 | 390.2 | 2104738.8 | 780.4 | 4209477.6 | 572 | 2571140 | 588 | 2643060 | 523 | 1 | 80 | 4495 | 175 | 4495 | 16 | 4495 | 96 | 4495 | 300 | 0 | 5277309.8 | 412956549 | 1174.04 | 91870.2
47 | Lodhran | Tube Well | Rural | 7022 | 405 | 121.5 | 853173 | 78 | 361.5 | 3046143.6 | 723 | 6092287.2 | 9 | 63198 | 30.1 | 211362.2 | 482 | 1 | 80 | 7022 | 175 | 7022 | 16 | 0 | 96 | 0 | 300 | 0 | 3962514.6 | 380778483 | 564.3 | 54226.5
48 | Lodhran | Benazir | Rural | 5179 | 450 | 135 | 699165 | 96 | 411 | 2554282.8 | 822 | 5108565.6 | 22 | 113938 | 44.3 | 229429.7 | 545 | 1 | 80 | 5179 | 175 | 5179 | 16 | 5179 | 96 | 0 | 300 | 0 | 3367385.8 | 322377213 | 650.2 | 62247
49 | Lodhran | Sal Sadar | Rural | 5250 | 343 | 102.9 | 540225 | 68 | 308.1 | 1941030 | 616.2 | 3882060 | 23 | 120750 | 128 | 672000 | 410 | 1 | 80 | 5250 | 175 | 5250 | 16 | 5250 | 96 | 5250 | 300 | 0 | 2602005 | 274864275 | 495.62 | 52355.1
50 | A.P East | Hatheji | Rural | 4039 | 160 | 48 | 193872 | 80 | 192 | 930585.6 | 384 | 1861171.2 | 9 | 36351 | 28 | 113092 | 240 | 0 | 80 | 4039 | 175 | 4039 | 16 | 0 | 96 | 0 | 300 | 0 | 1160808.6 | 119037408 | 287.4 | 29472
51 | A.P East | Khuram Pur | Rural | 2892 | 99 | 29.7 | 85892.4 | 12 | 81.3 | 282143.52 | 162.6 | 564287.04 | 21 | 60732 | 25 | 72300 | 111 | 0 | 80 | 2892 | 175 | 2892 | 16 | 2892 | 96 | 0 | 300 | 0 | 428767.92 | 38452899.6 | 148.26 | 13296.3
52 | A.P East | Kotla Mosa Khan | Rural | 5461 | 199 | 59.7 | 326021.7 | 135 | 274.3 | 1797542.76 | 548.6 | 3595085.52 | 4 | 21844 | 15 | 81915 | 334 | 0 | 80 | 5461 | 175 | 5461 | 16 | 0 | 96 | 0 | 300 | 0 | 2145408.46 | 221598096.3 | 392.86 | 40578.3
53 | A.P East | Nabi Pur | Rural | 2086 | 70 | 21 | 43806 | 15 | 64 | 160204.8 | 128 | 320409.6 | 26 | 54236 | 30 | 62580 | 85 | 0 | 80 | 2086 | 175 | 0 | 16 | 2086 | 96 | 0 | 300 | 0 | 258246.8 | 23110794 | 123.8 | 11079
54 | A.P East | Mehrab Wala | Rural | 5419 | 105 | 31.5 | 170698.5 | 45 | 118.5 | 770581.8 | 237 | 1541163.6 | 6 | 32514 | 20 | 108380 | 150 | 0 | 80 | 5419 | 175 | 5419 | 16 | 0 | 96 | 0 | 300 | 0 | 973794.3 | 99484711.5 | 179.7 | 18358.5
55 | A.P East | Khan Pur | Rural | 5366 | 111 | 33.3 | 178687.8 | 36 | 113.7 | 732137.04 | 227.4 | 1464274.08 | 6 | 32196 | 20 | 107320 | 147 | 0 | 80 | 5366 | 175 | 5366 | 16 | 0 | 96 | 0 | 300 | 0 | 943020.84 | 94831708.2 | 175.74 | 17672.7
56 | A.P East | Meerana | Rural | 5043 | 115 | 34.5 | 173983.5 | 51 | 131.5 | 795785.4 | 263 | 1591570.8 | 8 | 40344 | 25 | 126075 | 166 | 0 | 80 | 5043 | 175 | 5043 | 16 | 0 | 96 | 0 | 300 | 0 | 1010112.9 | 103580698.5 | 200.3 | 20539.5
57 | A.P East | Qila Darawar | Rural | 3533 | 99 | 29.7 | 104930.1 | 60 | 129.3 | 548180.28 | 258.6 | 1096360.56 | 8 | 28264 | 25 | 88325 | 159 | 0 | 80 | 3533 | 175 | 3533 | 16 | 0 | 96 | 0 | 300 | 0 | 681374.38 | 71395923.9 | 192.86 | 20208.3
58 | A.P East | Shahi Wala | Rural | 5991 | 105 | 31.5 | 188716.5 | 40 | 113.5 | 815974.2 | 227 | 1631948.4 | 10 | 59910 | 30 | 179730 | 145 | 0 | 80 | 5991 | 175 | 5991 | 16 | 0 | 96 | 0 | 300 | 0 | 1064600.7 | 109266853.5 | 177.7 | 18238.5
59 | A.P East | Tibbi Izzat | Rural | 3043 | 180 | 54 | 164322 | 40 | 166 | 606165.6 | 332 | 1212331.2 | 8 | 24344 | 30 | 91290 | 220 | 0 | 80 | 3043 | 175 | 3043 | 16 | 0 | 96 | 0 | 300 | 0 | 794831.6 | 78710238 | 261.2 | 25866
60 | A.P East | Klp Road | Rural | 4278 | 120 | 36 | 154008 | 35 | 119 | 610898.4 | 238 | 1221796.8 | 8 | 34224 | 21 | 89838 | 155 | 0 | 80 | 4278 | 175 | 4278 | 16 | 0 | 96 | 0 | 300 | 0 | 799130.4 | 79160112 | 186.8 | 18504
61 | A.P East | Mohind Wah | Rural | 5611 | 121 | 36.3 | 203679.3 | 65 | 149.7 | 1007960.04 | 299.4 | 2015920.08 | 4 | 22444 | 22 | 123442 | 186 | 0 | 80 | 5611 | 175 | 5611 | 16 | 0 | 96 | 0 | 300 | 0 | 1234083.34 | 128972762.7 | 219.94 | 22985.7
62 | A.P East | Mohsin Abad | Rural | 5710 | 178 | 53.4 | 304914 | 35 | 159.6 | 1093579.2 | 319.2 | 2187158.4 | 5 | 28550 | 21 | 119910 | 213 | 0 | 80 | 5710 | 175 | 5710 | 16 | 0 | 96 | 0 | 300 | 0 | 1427043.2 | 139338846 | 249.92 | 24402.6
63 | A.P East | TMP | Rural | 2671 | 48 | 14.4 | 38462.4 | 1 | 34.6 | 110899.92 | 69.2 | 221799.84 | 0 | 0 | 0 | 0 | 49 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 149362.32 | 13423377.6 | 55.92 | 5025.6
64 | A.P East | 32-more | Rural | 6338 | 152 | 45.6 | 289012.8 | 60 | 166.4 | 1265571.84 | 332.8 | 2531143.68 | 6 | 38028 | 27 | 171126 | 212 | 0 | 80 | 6338 | 175 | 6338 | 16 | 0 | 96 | 0 | 300 | 0 | 1592612.64 | 163003219.2 | 251.28 | 25718.4
65 | A.P East | Adda 13000 | Rural | 3556 | 78 | 23.4 | 83210.4 | 24 | 78.6 | 335401.92 | 157.2 | 670803.84 | 7 | 24892 | 23 | 81788 | 102 | 0 | 80 | 3556 | 175 | 3556 | 16 | 0 | 96 | 0 | 300 | 0 | 443504.32 | 45405141.6 | 124.72 | 12768.6
66 | A.P East | Head Rajkan | Rural | 9006 | 154 | 46.2 | 416077.2 | 99 | 206.8 | 2234928.96 | 413.6 | 4469857.92 | 9 | 81054 | 31 | 279186 | 253 | 0 | 80 | 9006 | 175 | 9006 | 16 | 0 | 96 | 0 | 300 | 0 | 2732060.16 | 286190866.8 | 303.36 | 31777.8
67 | A.P East | Noor Pur | Rural | 3775 | 140 | 42 | 158550 | 15 | 113 | 511890 | 226 | 1023780 | 9 | 33975 | 31 | 117025 | 155 | 0 | 80 | 3775 | 175 | 3775 | 16 | 0 | 96 | 0 | 300 | 0 | 704415 | 68923950 | 186.6 | 18258
68 | A.P East | Chak 14 | Rural | 1051 | 39 | 11.7 | 12296.7 | 9 | 36.3 | 45781.56 | 72.6 | 91563.12 | 4 | 4204 | 10 | 10510 | 48 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 62282.26 | 6161277.3 | 59.26 | 5862.3
69 | A.P East | Tibbi Data | Rural | 8151 | 145 | 43.5 | 354568.5 | 15 | 116.5 | 1139509.8 | 233 | 2279019.6 | 3 | 24453 | 8 | 65208 | 160 | 0 | 80 | 8151 | 175 | 8151 | 16 | 0 | 96 | 0 | 300 | 0 | 1518531.3 | 141717361.5 | 186.3 | 17386.5
70 | A.P East | City Hatheji | Rural | 6594 | 165 | 49.5 | 326403 | 15 | 130.5 | 1032620.4 | 261 | 2065240.8 | 2 | 13188 | 10 | 65940 | 180 | 0 | 80 | 6594 | 175 | 6594 | 16 | 0 | 96 | 0 | 300 | 0 | 1372211.4 | 128850057 | 208.1 | 19540.5
71 | A.P East | City-II | Rural | 3977 | 74 | 22.2 | 88289.4 | 33 | 84.8 | 404699.52 | 169.6 | 809399.04 | 5 | 19885 | 22 | 87494 | 107 | 0 | 80 | 3977 | 175 | 3977 | 16 | 0 | 96 | 0 | 300 | 0 | 512873.92 | 54078450.6 | 128.96 | 13597.8
72 | A.P East | Mahi Tibba | Rural | 2266 | 39 | 11.7 | 26512.2 | 15 | 42.3 | 115022.16 | 84.6 | 230044.32 | 3 | 6798 | 8 | 18128 | 54 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 148332.36 | 14969875.8 | 65.46 | 6606.3
73 | A.P East | Mud Pir Wah | Rural | 2921 | 120 | 36 | 105156 | 20 | 104 | 364540.8 | 208 | 729081.6 | 4 | 11684 | 11 | 32131 | 140 | 0 | 80 | 2921 | 175 | 2921 | 16 | 0 | 96 | 0 | 300 | 0 | 481380.8 | 45988224 | 164.8 | 15744
74 | A.P East | Pul Farooq Abad | Rural | 8275 | 201 | 60.3 | 498982.5 | 30 | 170.7 | 1695051 | 341.4 | 3390102 | 3 | 24825 | 8 | 66200 | 231 | 0 | 80 | 8275 | 175 | 8275 | 16 | 0 | 96 | 0 | 300 | 0 | 2218858.5 | 208875067.5 | 268.14 | 25241.7
75 | A.P East | Tibbi Hoot | Rural | 4223 | 84 | 25.2 | 106419.6 | 12 | 70.8 | 358786.08 | 141.6 | 717572.16 | 680 | 2871640 | 702 | 2964546 | 96 | 0 | 80 | 4223 | 175 | 0 | 16 | 4223 | 96 | 4223 | 300 | 0 | 3336845.68 | 221246348.4 | 790.16 | 52390.8
76 | A.P East | Hussaini Chowk | Rural | 3773 | 45 | 13.5 | 50935.5 | 3 | 34.5 | 156202.2 | 69 | 312404.4 | 60 | 226380 | 115 | 433895 | 48 | 0 | 80 | 0 | 175 | 0 | 16 | 3773 | 96 | 3773 | 300 | 0 | 433517.7 | 44930770.5 | 114.9 | 11908.5
77 | A.P East | Ismail Pur | Rural | 9018 | 54 | 16.2 | 146091.6 | 4 | 41.8 | 452342.88 | 83.6 | 904685.76 | 36 | 324648 | 45 | 405810 | 58 | 0 | 80 | 0 | 175 | 0 | 16 | 9018 | 96 | 0 | 300 | 0 | 923082.48 | 79068020.4 | 102.36 | 8767.8
78 | A.P East | Kotlan Sheikhan | Rural | 3134 | 84 | 25.2 | 78976.8 | 4 | 62.8 | 236178.24 | 125.6 | 472356.48 | 36 | 112824 | 41 | 128494 | 88 | 0 | 80 | 3134 | 175 | 0 | 16 | 3134 | 96 | 0 | 300 | 0 | 427979.04 | 36287959.2 | 136.56 | 11578.8
79 | A.P East | Muhammad Pur | Rural | 12476 | 89 | 26.7 | 333109.2 | 99 | 161.3 | 2414854.56 | 322.6 | 4829709.12 | 8 | 99808 | 22 | 274472 | 188 | 0 | 80 | 12476 | 175 | 12476 | 16 | 0 | 96 | 0 | 300 | 0 | 2847771.76 | 307250194.8 | 228.26 | 24627.3
80 | A.P East | Punjnad | Rural | 7595 | 98 | 29.4 | 223293 | 8 | 76.6 | 698132.4 | 153.2 | 1396264.8 | 20 | 151900 | 25 | 189875 | 106 | 0 | 80 | 7595 | 175 | 7595 | 16 | 7595 | 96 | 0 | 300 | 0 | 1073325.4 | 95838267 | 141.32 | 12618.6
81 | Model Town | Canal | Rural | 4478 | 450 | 135 | 604530 | 67 | 382 | 2052715.2 | 764 | 4105430.4 | 7 | 31346 | 14 | 62692 | 517 | 0 | 80 | 4478 | 175 | 4478 | 16 | 0 | 96 | 0 | 300 | 0 | 2688591.2 | 251900934 | 600.4 | 56253
82 | Model Town | Goth Mehrab | Rural | 5652 | 69 | 20.7 | 116996.4 | 6 | 54.3 | 368284.32 | 108.6 | 736568.64 | 5 | 28260 | 14 | 79128 | 75 | 0 | 80 | 5652 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 513540.72 | 49292787.6 | 90.86 | 8721.3
83 | Model Town | Hakra | Rural | 1393 | 135 | 40.5 | 56416.5 | 12 | 106.5 | 178025.4 | 213 | 356050.8 | 4 | 5572 | 14 | 19502 | 147 | 0 | 80 | 1393 | 175 | 1393 | 16 | 0 | 96 | 0 | 300 | 0 | 240013.9 | 22702417.5 | 172.3 | 16297.5
84 | Model Town | Kalanch Wala | Rural | 2830 | 120 | 36 | 101880 | 9 | 93 | 315828 | 186 | 631656 | 3 | 8490 | 12 | 33960 | 129 | 0 | 80 | 2830 | 175 | 2830 | 16 | 0 | 96 | 0 | 300 | 0 | 426198 | 40242600 | 150.6 | 14220
85 | Model Town | Musafir Khana | Rural | 5408 | 74 | 22.2 | 120057.6 | 11 | 62.8 | 407546.88 | 125.6 | 815093.76 | 4 | 21632 | 9 | 48672 | 85 | 0 | 80 | 5408 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 549236.48 | 52186118.4 | 101.56 | 9649.8
86 | Model Town | Noor_pur | Rural | 2303 | 271 | 81.3 | 187233.9 | 43 | 232.7 | 643089.72 | 465.4 | 1286179.44 | 2 | 4606 | 11 | 25333 | 42 | 0 | 80 | 2303 | 175 | 2303 | 16 | 0 | 96 | 0 | 300 | 0 | 834929.62 | 79252448.1 | 362.54 | 34412.7
87 | Model Town | Noshehra Jadeed | Rural | 2597 | 98 | 29.4 | 76351.8 | 12 | 80.6 | 251181.84 | 161.2 | 502363.68 | 4 | 10388 | 9 | 23373 | 110 | 0 | 80 | 2597 | 175 | 2597 | 16 | 0 | 96 | 0 | 300 | 0 | 337921.64 | 31773256.2 | 130.12 | 12234.6
88 | Model Town | Rungpur | Rural | 6953 | 78 | 23.4 | 162700.2 | 14 | 68.6 | 572370.96 | 137.2 | 1144741.92 | 7 | 48671 | 11 | 76483 | 92 | 0 | 80 | 6953 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 783742.16 | 73761595.8 | 112.72 | 10608.6
89 | Model Town | Wasaib | Rural | 4426 | 390 | 117 | 517842 | 68 | 341 | 1811119.2 | 682 | 3622238.4 | 6 | 26556 | 22 | 97372 | 458 | 0 | 80 | 4426 | 175 | 4426 | 16 | 0 | 96 | 0 | 300 | 0 | 2355517.2 | 224730150 | 532.2 | 50775
90 | Model Town | Zakhira | Rural | 6302 | 593 | 177.9 | 1121125.8 | 108 | 523.1 | 3955891.44 | 1046.2 | 7911782.88 | 19 | 119738 | 96 | 604992 | 227 | 1 | 80 | 6302 | 175 | 6302 | 16 | 6302 | 96 | 0 | 300 | 0 | 5196755.24 | 514369870.2 | 824.62 | 81620.1
91 | Model Town | 13- Bc | Rural | 3580 | 120 | 36 | 128880 | 19 | 103 | 442488 | 206 | 884976 | 25 | 89500 | 28 | 100240 | 139 | 0 | 80 | 3580 | 175 | 3580 | 16 | 3580 | 96 | 0 | 300 | 0 | 660868 | 59499600 | 184.6 | 16620
92 | Model Town | Chak No. 12/bc | Rural | 7323 | 168 | 50.4 | 369079.2 | 18 | 135.6 | 1191598.56 | 271.2 | 2383197.12 | 2 | 14646 | 90 | 659070 | 186 | 0 | 80 | 7323 | 175 | 7323 | 16 | 0 | 96 | 0 | 300 | 0 | 1575323.76 | 183643264.8 | 215.12 | 25077.6
93 | Model Town | Ghani Pur | Rural | 5378 | 216 | 64.8 | 348494.4 | 110 | 261.2 | 1685680.32 | 522.4 | 3371360.64 | 7 | 37646 | 29 | 155962 | 326 | 0 | 80 | 5378 | 175 | 5378 | 16 | 0 | 96 | 0 | 300 | 0 | 2071820.72 | 212684841.6 | 385.24 | 39547.2
94 | Hasil Pur | Jamal Pur | Rural | 6626 | 236 | 70.8 | 469120.8 | 25 | 190.2 | 1512318.24 | 380.4 | 3024636.48 | 104 | 689104 | 125 | 828250 | 261 | 0 | 80 | 6626 | 175 | 6626 | 16 | 6626 | 96 | 6626 | 300 | 0 | 2670543.04 | 232580551.2 | 403.04 | 35101.2
95 | Hasil Pur | Qalamdar Pur | Rural | 2866 | 98 | 29.4 | 84260.4 | 16 | 84.6 | 290956.32 | 169.2 | 581912.64 | 50 | 143300 | 111 | 318126 | 114 | 0 | 80 | 2866 | 175 | 2866 | 16 | 2866 | 96 | 2866 | 300 | 0 | 518516.72 | 54255099.6 | 180.92 | 18930.6
96 | Hasil Pur | Shah Pur | Rural | 6746 | 190 | 57 | 384522 | 15 | 148 | 1198089.6 | 296 | 2396179.2 | 102 | 688092 | 150 | 1011900 | 205 | 0 | 80 | 6746 | 175 | 6746 | 16 | 6746 | 96 | 6746 | 300 | 0 | 2270703.6 | 205638318 | 336.6 | 30483
97 | Hasil Pur | Tube Well | Rural | 3336 | 160 | 48 | 160128 | 26 | 138 | 552441.6 | 276 | 1104883.2 | 141 | 470376 | 158 | 527088 | 186 | 0 | 80 | 3336 | 175 | 3336 | 16 | 3336 | 96 | 3336 | 300 | 0 | 1182945.6 | 98398656 | 354.6 | 29496
98 | Hasil Pur | Jhoke Sathu | Rural | 1655 | 202 | 60.6 | 100293 | 8 | 149.4 | 296708.4 | 298.8 | 593416.8 | 65 | 107575 | 166 | 274730 | 210 | 0 | 80 | 1655 | 175 | 1655 | 16 | 1655 | 96 | 1655 | 300 | 0 | 504576.4 | 52389687 | 304.88 | 31655.4
99 | Hasil Pur | Israni | Rural | 4618 | 338 | 101.4 | 468265.2 | 27 | 263.6 | 1460765.76 | 527.2 | 2921531.52 | 63 | 290934 | 240 | 1108320 | 365 | 0 | 80 | 4618 | 175 | 4618 | 16 | 4618 | 96 | 4618 | 300 | 0 | 2219964.96 | 243195886.8 | 480.72 | 52662.6
100 | Hasil Pur | K.k Bukhsh | Rural | 2654 | 230 | 69 | 183126 | 25 | 186 | 592372.8 | 372 | 1184745.6 | 41 | 108814 | 115 | 305210 | 255 | 0 | 80 | 2654 | 175 | 2654 | 16 | 2654 | 96 | 2654 | 300 | 0 | 884312.8 | 89946714 | 333.2 | 33891
101 | Hasil Pur | Kotla qaim khan | Rural | 5501 | 275 | 82.5 | 453832.5 | 23 | 215.5 | 1422558.6 | 431 | 2845117.2 | 52 | 286052 | 154 | 847154 | 298 | 0 | 80 | 5501 | 175 | 5501 | 16 | 5501 | 96 | 5501 | 300 | 0 | 2162443.1 | 222897769.5 | 393.1 | 40519.5
102 | Hasil Pur | Goth Mitha | Rural | 2264 | 222 | 66.6 | 150782.4 | 32 | 187.4 | 509128.32 | 374.8 | 1018256.64 | 57 | 129048 | 221 | 500344 | 254 | 0 | 80 | 2264 | 175 | 2264 | 16 | 2264 | 96 | 2264 | 300 | 0 | 788958.72 | 91568385.6 | 348.48 | 40445.4
103 | Hasil Pur | Tube Well | Rural | 1615 | 298 | 89.4 | 144381 | 24 | 232.6 | 450778.8 | 465.2 | 901557.6 | 103 | 166345 | 326 | 526490 | 322 | 0 | 80 | 1615 | 175 | 1615 | 16 | 1615 | 96 | 1615 | 300 | 0 | 761504.8 | 86115999 | 471.52 | 53322.6
104 | Hasil Pur | Al Tahir | Rural | 6377 | 180 | 54 | 344358 | 16 | 142 | 1086640.8 | 284 | 2173281.6 | 92 | 586684 | 125 | 797125 | 196 | 0 | 80 | 6377 | 175 | 6377 | 16 | 6377 | 96 | 6377 | 300 | 0 | 2017682.8 | 179257470 | 316.4 | 28110
105 | Hasil Pur | Al-fateh | Rural | 3723 | 67 | 20.1 | 74832.3 | 4 | 50.9 | 227400.84 | 101.8 | 454801.68 | 32 | 119136 | 44 | 163812 | 71 | 0 | 80 | 3723 | 175 | 0 | 16 | 3723 | 96 | 0 | 300 | 0 | 421369.14 | 37341317.7 | 113.18 | 10029.9
106 | Hasil Pur | Al-haider | Rural | 4556 | 109 | 32.7 | 148981.2 | 5 | 81.3 | 444483.36 | 162.6 | 888966.72 | 41 | 186796 | 73 | 332588 | 114 | 0 | 80 | 4556 | 175 | 4556 | 16 | 4556 | 96 | 0 | 300 | 0 | 780260.56 | 73740226.8 | 171.26 | 16185.3
107 | Hasil Pur | M/pannah | Rural | 5800 | 109 | 32.7 | 189660 | 8 | 84.3 | 586728 | 168.6 | 1173456 | 69 | 400200 | 100 | 580000 | 117 | 0 | 80 | 5800 | 175 | 5800 | 16 | 5800 | 96 | 5800 | 300 | 0 | 1176588 | 105776340 | 202.86 | 18237.3
108 | Hasil Pur | satluj | Rural | 5567 | 93 | 27.9 | 155319.3 | 11 | 76.1 | 508378.44 | 152.2 | 1016756.88 | 110 | 612370 | 102 | 567834 | 104 | 0 | 80 | 5567 | 175 | 5567 | 16 | 5567 | 96 | 5567 | 300 | 0 | 1276067.74 | 95541410.7 | 229.22 | 17162.1
109 | Hasil Pur | Sarwar Kot | Rural | 1320 | 1 | 0.3 | 396 | 1 | 1.7 | 2692.8 | 3.4 | 5385.6 | 10 | 13200 | 44 | 58080 | 2 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 16288.8 | 3809124 | 12.34 | 2885.7
110 | Hasil Pur | Anayti | Rural | 6950 | 134 | 40.2 | 279390 | 12 | 105.8 | 882372 | 211.6 | 1764744 | 72 | 500400 | 136 | 945200 | 146 | 0 | 80 | 6950 | 175 | 6950 | 16 | 6950 | 96 | 6950 | 300 | 0 | 1662162 | 163434810 | 239.16 | 23515.8
111 | Hasil Pur | Kabira Pully | Rural | 4418 | 288 | 86.4 | 381715.2 | 25 | 226.6 | 1201342.56 | 453.2 | 2402685.12 | 28 | 123704 | 86 | 379948 | 313 | 0 | 80 | 4418 | 175 | 4418 | 16 | 4418 | 96 | 0 | 300 | 0 | 1706761.76 | 168103132.8 | 386.32 | 38049.6
112 | Hasil Pur | Kot_azam | Rural | 7703 | 479 | 143.7 | 1106921.1 | 29 | 364.3 | 3367443.48 | 728.6 | 6734886.96 | 30 | 231090 | 89 | 685567 | 508 | 0 | 80 | 7703 | 175 | 7703 | 16 | 7703 | 96 | 0 | 300 | 0 | 4705454.58 | 448548000.9 | 610.86 | 58230.3
113 | Hasil Pur | Qaimpur | Rural | 3340 | 165 | 49.5 | 165330 | 14 | 129.5 | 519036 | 259 | 1038072 | 36 | 120240 | 102 | 340680 | 179 | 0 | 80 | 3340 | 175 | 3340 | 16 | 3340 | 96 | 3340 | 300 | 0 | 804606 | 83221110 | 240.9 | 24916.5
114 | Hasil Pur | Sheikh Wahan | Rural | 2892 | 153 | 45.9 | 132742.8 | 13 | 120.1 | 416795.04 | 240.2 | 833590.08 | 56 | 161952 | 112 | 323904 | 166 | 0 | 80 | 2892 | 175 | 2892 | 16 | 2892 | 96 | 2892 | 300 | 0 | 711489.84 | 69847873.2 | 246.02 | 24152.1
115 | Kahror Pacca | Ali Sher | Rural | 3522 | 368 | 110.4 | 388828.8 | 17 | 274.6 | 1160569.44 | 549.2 | 2321138.88 | 145 | 510690 | 305 | 1074210 | 385 | 0 | 80 | 3522 | 175 | 3522 | 16 | 3522 | 96 | 3522 | 300 | 0 | 2060088.24 | 204887419.2 | 584.92 | 58173.6
116 | Kahror Pacca | Sadiq Shaheed | Rural | 2662 | 87 | 26.1 | 69478.2 | 5 | 65.9 | 210510.96 | 131.8 | 421021.92 | 25 | 66550 | 33 | 87846 | 92 | 0 | 80 | 2662 | 175 | 0 | 16 | 2662 | 96 | 0 | 300 | 0 | 346539.16 | 30740509.8 | 130.18 | 11547.9
117 | Kahror Pacca | Khushi Muhammad | Rural | 3716 | 203 | 60.9 | 226304.4 | 7 | 149.1 | 664866.72 | 298.2 | 1329733.44 | 109 | 405044 | 223 | 828668 | 210 | 0 | 80 | 3716 | 175 | 3716 | 16 | 3716 | 96 | 3716 | 300 | 0 | 1296215.12 | 130182999.6 | 348.82 | 35033.1
118 | Kahror Pacca | Thatta Road | Rural | 3626 | 313 | 93.9 | 340481.4 | 21 | 240.1 | 1044723.12 | 480.2 | 2089446.24 | 142 | 514892 | 238 | 862988 | 334 | 0 | 80 | 3626 | 175 | 3626 | 16 | 3626 | 96 | 3626 | 300 | 0 | 1900096.52 | 178167498.6 | 524.02 | 49136.1
119 | Kahror Pacca | Chak 227 Wb | Rural | 2025 | 131 | 39.3 | 79582.5 | 15 | 106.7 | 259281 | 213.4 | 518562 | 125 | 253125 | 133 | 269325 | 146 | 0 | 80 | 2025 | 175 | 2025 | 16 | 2025 | 96 | 2025 | 300 | 0 | 591988.5 | 47511967.5 | 292.34 | 23462.7
120 | Kahror Pacca | Ghulam Rasool | Rural | 3039 | 233 | 69.9 | 212426.1 | 12 | 175.1 | 638554.68 | 350.2 | 1277109.36 | 379 | 1151781 | 463 | 1407057 | 245 | 0 | 80 | 3039 | 175 | 3039 | 16 | 3039 | 96 | 3039 | 300 | 0 | 2002761.78 | 161687259.9 | 659.02 | 53204.1
121 | Kahror Pacca | Nasrullah Tareen | Rural | 3829 | 306 | 91.8 | 351502.2 | 20 | 234.2 | 1076102.16 | 468.4 | 2152204.32 | 88 | 336952 | 216 | 827064 | 326 | 0 | 80 | 3829 | 175 | 3829 | 16 | 3829 | 96 | 3829 | 300 | 0 | 1764556.36 | 179810605.8 | 460.84 | 46960.2
122 | Kahror Pacca | Noor Garh | Rural | 6318 | 285 | 85.5 | 540189 | 24 | 223.5 | 1694487.6 | 447 | 3388975.2 | 123 | 777114 | 137 | 865566 | 309 | 0 | 80 | 6318 | 175 | 6318 | 16 | 6318 | 96 | 6318 | 300 | 0 | 3011790.6 | 256893039 | 476.7 | 40660.5
123 | Kahror Pacca | Qutabpur | Rural | 5844 | 253 | 75.9 | 443559.6 | 17 | 194.1 | 1361184.48 | 388.2 | 2722368.96 | 126 | 736344 | 245 | 1431780 | 270 | 0 | 80 | 5844 | 175 | 5844 | 16 | 5844 | 96 | 5844 | 300 | 0 | 2541088.08 | 250579616.4 | 434.82 | 42878.1
124 | Kahror Pacca | Sadat | Rural | 4007 | 286 | 85.8 | 343800.6 | 15 | 215.2 | 1034767.68 | 430.4 | 2069535.36 | 237 | 949659 | 227 | 909589 | 301 | 0 | 80 | 4007 | 175 | 4007 | 16 | 4007 | 96 | 4007 | 300 | 0 | 2328227.28 | 179778863.4 | 581.04 | 44866.2
125 | Kahror Pacca | Zakheera | Rural | 6628 | 296 | 88.8 | 588566.4 | 15 | 222.2 | 1767289.92 | 444.4 | 3534579.84 | 111 | 735708 | 140 | 927920 | 311 | 0 | 80 | 6628 | 175 | 6628 | 16 | 6628 | 96 | 6628 | 300 | 0 | 3091564.32 | 269515689.6 | 466.44 | 40663.2
126 | Kahror Pacca | Factory | Rural | 9964 | 561 | 168.3 | 1676941.2 | 31 | 423.7 | 5066096.16 | 847.4 | 10132192.32 | 78 | 777192 | 85 | 846940 | 592 | 0 | 80 | 9964 | 175 | 9964 | 16 | 9964 | 96 | 0 | 300 | 0 | 7520229.36 | 663778762.8 | 754.74 | 66617.7
127 | Kahror Pacca | Suhail Pur | Rural | 1942 | 432 | 129.6 | 251683.2 | 27 | 329.4 | 767633.76 | 658.8 | 1535267.52 | 70 | 135940 | 90 | 174780 | 459 | 0 | 80 | 1942 | 175 | 1942 | 16 | 1942 | 96 | 0 | 300 | 0 | 1155256.96 | 103357900.8 | 594.88 | 53222.4
128 | Kahror Pacca | Ali Pur | Rural | 4277 | 274 | 82.2 | 351569.4 | 15 | 206.8 | 1061380.32 | 413.6 | 2122760.64 | 86 | 367822 | 134 | 573118 | 289 | 0 | 80 | 4277 | 175 | 4277 | 16 | 4277 | 96 | 4277 | 300 | 0 | 1780771.72 | 162807426.6 | 416.36 | 38065.8
129 | Kahror Pacca | Bukhari Wahin | Rural | 4088 | 343 | 102.9 | 420655.2 | 22 | 262.1 | 1285757.76 | 524.2 | 2571515.52 | 98 | 400624 | 156 | 637728 | 365 | 0 | 80 | 4088 | 175 | 4088 | 16 | 4088 | 96 | 4088 | 300 | 0 | 2107036.96 | 193816576.8 | 515.42 | 47411.1
130 | Kahror Pacca | Fateh Shah | Rural | 3610 | 329 | 98.7 | 356307 | 24 | 254.3 | 1101627.6 | 508.6 | 2203255.2 | 114 | 411540 | 184 | 664240 | 353 | 0 | 80 | 3610 | 175 | 3610 | 16 | 3610 | 96 | 3610 | 300 | 0 | 1869474.6 | 173118633 | 517.86 | 47955.3
131 | Kahror Pacca | Goth Bahar | Rural | 3140 | 287 | 86.1 | 270354 | 14 | 214.9 | 809743.2 | 429.8 | 1619486.4 | 189 | 593460 | 115 | 361100 | 301 | 0 | 80 | 3140 | 175 | 3140 | 16 | 3140 | 96 | 3140 | 300 | 0 | 1673557.2 | 119646246 | 532.98 | 38103.9
132 | Kahror Pacca | Inayat Ali | Rural | 4607 | 420 | 126 | 580482 | 18 | 312 | 1724860.8 | 624 | 3449721.6 | 92 | 423844 | 232 | 1068824 | 438 | 0 | 80 | 4607 | 175 | 4607 | 16 | 4607 | 96 | 4607 | 300 | 0 | 2729186.8 | 272854182 | 592.4 | 59226
133 | Kahror Pacca | Mangwani | Rural | 2519 | 431 | 129.3 | 325706.7 | 29 | 330.7 | 999639.96 | 661.4 | 1999279.92 | 200 | 503800 | 162 | 408078 | 460 | 0 | 80 | 2519 | 175 | 2519 | 16 | 2519 | 96 | 2519 | 300 | 0 | 1829146.66 | 145418595.3 | 726.14 | 57728.7
134 | Kahror Pacca | Mehar Shah | Rural | 2789 | 304 | 91.2 | 254356.8 | 17 | 229.8 | 769094.64 | 459.6 | 1538189.28 | 89 | 248221 | 171 | 476919 | 321 | 0 | 80 | 2789 | 175 | 2789 | 16 | 2789 | 96 | 2789 | 300 | 0 | 1271672.44 | 121669567.2 | 455.96 | 43624.8
135 | Kahror Pacca | Shahpur | Rural | 1988 | 396 | 118.8 | 236174.4 | 32 | 309.2 | 737627.52 | 618.4 | 1475255.04 | 118 | 234584 | 186 | 369768 | 428 | 0 | 80 | 1988 | 175 | 1988 | 16 | 1988 | 96 | 1988 | 300 | 0 | 1208385.92 | 111409905.6 | 607.84 | 56041.2
136 | Kahror Pacca | Burhan Pur | Rural | 5275 | 592 | 177.6 | 936840 | 39 | 453.4 | 2870022 | 906.8 | 5740044 | 174 | 917850 | 162 | 854550 | 631 | 0 | 80 | 5275 | 175 | 5275 | 16 | 5275 | 96 | 5275 | 300 | 0 | 4724712 | 398486160 | 895.68 | 75542.4
137 | Kahror Pacca | Nao Qabal Wah | Rural | 5046 | 585 | 175.5 | 885573 | 30 | 439.5 | 2661260.4 | 879 | 5322520.8 | 120 | 605520 | 177 | 893142 | 615 | 0 | 80 | 5046 | 175 | 5046 | 16 | 5046 | 96 | 5046 | 300 | 0 | 4152353.4 | 375596487 | 822.9 | 74434.5
138 | Kahror Pacca | Qadir Pur Cheema | Rural | 7483 | 564 | 169.2 | 1266123.6 | 32 | 426.8 | 3832493.28 | 853.6 | 7664986.56 | 130 | 972790 | 204 | 1526532 | 596 | 0 | 80 | 7483 | 175 | 7483 | 16 | 7483 | 96 | 7483 | 300 | 0 | 6071406.88 | 555289484.4 | 811.36 | 74206.8
139 | Kahror Pacca | Satluj | Rural | 3862 | 639 | 191.7 | 740345.4 | 24 | 471.3 | 2184192.72 | 942.6 | 4368385.44 | 369 | 1425078 | 257 | 992534 | 663 | 0 | 80 | 3862 | 175 | 3862 | 16 | 3862 | 96 | 3862 | 300 | 0 | 4349616.12 | 323876202.6 | 1126.26 | 83862.3
140 | Kahror Pacca | Shah Muhammad | Rural | 4111 | 396 | 118.8 | 488386.8 | 32 | 309.2 | 1525345.44 | 618.4 | 3050690.88 | 118 | 485098 | 171 | 702981 | 428 | 0 | 80 | 4111 | 175 | 4111 | 16 | 4111 | 96 | 4111 | 300 | 0 | 2498830.24 | 226685473.2 | 607.84 | 55141.2
|  | TOTAL |  | 533227 | 24732 | 7419.6 | 33289177.5 | 5127 | 22439.4 | 122132211 | 44878.8 | 244264422 |  | 22363024 | 9530.55 | 39926963.75 | 36644 | 21 | 80 | 511907 | 175 | 478066 | 16 | 211146 | 96 | 134336 | 300 | 0 | 177784412.5 | 17151350677.5 | 333.4122 | 32165.1955

## 400-220 (Rural) Sahiwal
Statement of 400/220 V MEPCO Consumers For 2020-21
Sahiwal Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | Sahiwal-1 | Korey Shah | Rural | 4724 | 365 | 109.5 | 517278 | 25 | 280.5 | 1590098.4 | 561 | 3180196.8 | 76 | 359024 | 86.07 | 406594.68 | 390 | 0 | 80 | 4724 | 175 | 4724 | 16 | 4724 | 96 | 0 | 300 | 0 | 2466400.4 | 216759322.8 | 522.1 | 45884.7
2 | Sahiwal-1 | 65GD Yaray Wala | Rural | 5725 | 370 | 111 | 635475 | 24 | 283 | 1944210 | 566 | 3888420 | 71 | 406475 | 85.57 | 489888.25 | 394 | 0 | 80 | 5725 | 175 | 5725 | 16 | 5725 | 96 | 0 | 300 | 0 | 2986160 | 264604920 | 521.6 | 46219.2
3 | Sahiwal-1 | Maiz Farm | Rural | 7055 | 265 | 79.5 | 560872.5 | 22 | 207.5 | 1756695 | 415 | 3513390 | 65 | 458575 | 72 | 507960 | 287 | 0 | 80 | 7055 | 175 | 7055 | 16 | 7055 | 96 | 0 | 300 | 0 | 2776142.5 | 242963617.5 | 393.5 | 34438.5
4 | Sahiwal-1 | Madhali Sharif | Rural | 4619 | 153 | 45.9 | 212012.1 | 14 | 121.1 | 671233.08 | 242.2 | 1342466.16 | 71 | 327949 | 91.26 | 421529.94 | 167 | 0 | 80 | 4619 | 175 | 4619 | 16 | 4619 | 96 | 0 | 300 | 0 | 1211194.18 | 106475802.3 | 262.22 | 23051.7
5 | Sahiwal-1 | Qutab Shahana | Rural | 5580 | 238 | 71.4 | 398412 | 10 | 176.6 | 1182513.6 | 353.2 | 2365027.2 | 42 | 234360 | 85.29 | 475918.2 | 248 | 0 | 80 | 5580 | 175 | 5580 | 16 | 5580 | 96 | 0 | 300 | 0 | 1815285.6 | 171651960 | 325.32 | 30762
6 | Sahiwal-1 | Murshad Abad | Rural | 4533 | 119 | 35.7 | 161828.1 | 7 | 90.3 | 491195.88 | 180.6 | 982391.76 | 41 | 185853 | 68.3 | 309603.9 | 126 | 0 | 80 | 4533 | 175 | 4533 | 16 | 4533 | 96 | 0 | 300 | 0 | 838876.98 | 78005223.9 | 185.06 | 17208.3
7 | Sahiwal-1 | Booti Pall | Rural | 2524 | 167 | 50.1 | 126452.4 | 7 | 123.9 | 375268.32 | 247.8 | 750536.64 | 46 | 116104 | 91.2 | 230188.8 | 174 | 0 | 80 | 2524 | 175 | 2524 | 16 | 2524 | 96 | 0 | 300 | 0 | 617824.72 | 59222883.6 | 244.78 | 23463.9
8 | Sahiwal-1 | Abdullah Shah | Rural | 5668 | 264 | 79.2 | 448905.6 | 11 | 195.8 | 1331753.28 | 391.6 | 2663506.56 | 52 | 294736 | 90.33 | 511990.44 | 275 | 0 | 80 | 5668 | 175 | 5668 | 16 | 5668 | 96 | 0 | 300 | 0 | 2075394.88 | 191876536.8 | 366.16 | 33852.6
9 | Sahiwal-1 | Shahmadar | Rural | 5679 | 240 | 72 | 408888 | 5 | 173 | 1178960.4 | 346 | 2357920.8 | 58 | 329382 | 97.17 | 551828.43 | 245 | 0 | 80 | 5679 | 175 | 5679 | 16 | 5679 | 96 | 5679 | 300 | 0 | 1917230.4 | 175811617.8 | 337.6 | 30958.2
10 | Sahiwal-1 | Qadir Abad | Rural | 7302 | 445 | 133.5 | 974817 | 15 | 326.5 | 2860923.6 | 653 | 5721847.2 | 67 | 489234 | 112.29 | 819941.58 | 460 | 0 | 80 | 7302 | 175 | 7302 | 16 | 7302 | 96 | 7302 | 300 | 0 | 4324974.6 | 395431777.8 | 592.3 | 54153.9
11 | Sahiwal-1 | Hafiz Dayim | Rural | 8183 | 404 | 121.2 | 991779.6 | 13 | 295.8 | 2904637.68 | 591.6 | 5809275.36 | 71 | 580993 | 103.4 | 846122.2 | 417 | 0 | 80 | 8183 | 175 | 8183 | 16 | 8183 | 96 | 8183 | 300 | 0 | 4477410.28 | 402299192.4 | 547.16 | 49162.8
12 | Sahiwal-1 | 46/5-L | Rural | 7295 | 352 | 105.6 | 770352 | 10 | 256.4 | 2244525.6 | 512.8 | 4489051.2 | 62 | 452290 | 68 | 496060 | 362 | 0 | 80 | 7295 | 175 | 7295 | 16 | 7295 | 96 | 0 | 300 | 0 | 3467167.6 | 301417728 | 475.28 | 41318.4
13 | Sahiwal-1 | Khan Kamal | Rural | 7653 | 386 | 115.8 | 886217.4 | 12 | 282.2 | 2591611.92 | 564.4 | 5183223.84 | 66 | 505098 | 122.56 | 937951.68 | 398 | 0 | 80 | 7653 | 175 | 7653 | 16 | 7653 | 96 | 7653 | 300 | 0 | 3982927.32 | 369929183.4 | 520.44 | 48337.8
14 | Sahiwal-1 | Noor Shah | Rural | 9048 | 460 | 138 | 1248624 | 21 | 343 | 3724156.8 | 686 | 7448313.6 | 87 | 787176 | 100.37 | 908147.76 | 481 | 0 | 80 | 9048 | 175 | 9048 | 16 | 9048 | 96 | 9048 | 300 | 0 | 5759956.8 | 505133553.6 | 636.6 | 55828.2
15 | Sahiwal-2nd | Gunj Shakar | Rural | 4981 | 354 | 106.2 | 528982.2 | 19 | 266.8 | 1594716.96 | 533.6 | 3189433.92 | 74 | 368594 | 98 | 488138 | 373 | 0 | 80 | 4981 | 175 | 4981 | 16 | 4981 | 96 | 4981 | 300 | 0 | 2492293.16 | 222241261.8 | 500.36 | 44617.8
16 | Sahiwal-2nd | Balhe Wala | Rural | 4792 | 253 | 75.9 | 363712.8 | 120 | 297.1 | 1708443.84 | 594.2 | 3416887.68 | 10 | 47920 | 44 | 210848 | 373 | 0 | 80 | 4792 | 175 | 4792 | 16 | 0 | 96 | 0 | 300 | 0 | 2120076.64 | 218755279.2 | 442.42 | 45650.1
17 | Sahiwal-2nd | Halla | Rural | 3880 | 482 | 144.6 | 561048 | 18 | 355.4 | 1654742.4 | 710.8 | 3309484.8 | 30 | 116400 | 47.42 | 183989.6 | 499 | 1 | 80 | 3880 | 175 | 3880 | 16 | 3880 | 96 | 0 | 300 | 0 | 2332190.4 | 211291608 | 601.08 | 54456.6
18 | Sahiwal-2nd | Budh Dhakoo | Rural | 5735 | 244 | 73.2 | 419802 | 118 | 288.8 | 1987521.6 | 577.6 | 3975043.2 | 8 | 45880 | 52 | 298220 | 362 | 0 | 80 | 5735 | 175 | 5735 | 16 | 0 | 96 | 0 | 300 | 0 | 2453203.6 | 257655198 | 427.76 | 44926.8
19 | Sahiwal-2nd | Khawaja Arif | Rural | 7139 | 317 | 95.1 | 678918.9 | 160 | 381.9 | 3271660.92 | 763.8 | 6543321.84 | 12 | 85668 | 56 | 399784 | 477 | 0 | 80 | 7139 | 175 | 7139 | 16 | 0 | 96 | 0 | 300 | 0 | 4036247.82 | 418623107.1 | 565.38 | 58638.9
20 | Sahiwal-2nd | Dera Raheem | Rural | 8968 | 501 | 150.3 | 1347890.4 | 150 | 500.7 | 5388333.12 | 1001.4 | 10776666.24 | 13 | 116584 | 57 | 511176 | 651 | 0 | 80 | 8968 | 175 | 8968 | 16 | 0 | 96 | 0 | 300 | 0 | 6852807.52 | 681314205.6 | 764.14 | 75971.7
21 | Sahiwal-2nd | Dairy | Rural | 3903 | 272 | 81.6 | 318484.8 | 131 | 321.4 | 1505309.04 | 642.8 | 3010618.08 | 8 | 31224 | 43 | 167829 | 403 | 0 | 80 | 3903 | 175 | 3903 | 16 | 0 | 96 | 0 | 300 | 0 | 1855017.84 | 191662279.2 | 475.28 | 49106.4
22 | Sahiwal-2nd | Khaki Shah | Rural | 5173 | 364 | 109.2 | 564891.6 | 16 | 270.8 | 1681018.08 | 541.6 | 3362036.16 | 48 | 248304 | 62.1 | 321243.3 | 380 | 0 | 80 | 5173 | 175 | 5173 | 16 | 5173 | 96 | 0 | 300 | 0 | 2494213.68 | 222691442.4 | 482.16 | 43048.8
23 | Sahiwal-2nd | Shah Murad | Rural | 4630 | 250 | 75 | 347250 | 13 | 188 | 1044528 | 376 | 2089056 | 24 | 111120 | 40.15 | 185894.5 | 263 | 0 | 80 | 4630 | 175 | 4630 | 16 | 4630 | 96 | 0 | 300 | 0 | 1502898 | 137538780 | 324.6 | 29706
24 | Sahiwal-2nd | Ganjibar | Rural | 5876 | 240 | 72 | 423072 | 12 | 180 | 1269216 | 360 | 2538432 | 15 | 88140 | 25.3 | 148662.8 | 252 | 0 | 80 | 5876 | 175 | 5876 | 16 | 0 | 96 | 0 | 300 | 0 | 1780428 | 162494904 | 303 | 27654
25 | Sahiwal-2nd | Ehsan Abad | Rural | 5694 | 370 | 111 | 632034 | 8 | 267 | 1824357.6 | 534 | 3648715.2 | 36 | 204984 | 15.4 | 87687.6 | 378 | 0 | 80 | 5694 | 175 | 5694 | 16 | 5694 | 96 | 0 | 300 | 0 | 2661375.6 | 226080270 | 467.4 | 39705
26 | Sahiwal-2nd | Nai Wala | Rural | 5666 | 384 | 115.2 | 652723.2 | 3 | 271.8 | 1848022.56 | 543.6 | 3696045.12 | 38 | 215308 | 30.15 | 170829.9 | 387 | 0 | 80 | 5666 | 175 | 5666 | 16 | 5666 | 96 | 0 | 300 | 0 | 2716053.76 | 233970670.8 | 479.36 | 41293.8
27 | Sahiwal-2nd | Sahiwal Road | Rural | 4949 | 264 | 79.2 | 391960.8 | 6 | 190.8 | 1133123.04 | 381.6 | 2266246.08 | 28 | 138572 | 5.4 | 26724.6 | 270 | 0 | 80 | 4949 | 175 | 4949 | 16 | 4949 | 96 | 0 | 300 | 0 | 1663655.84 | 138754123.2 | 336.16 | 28036.8
28 | Sahiwal-2nd | Harappa City | Rural | 10822 | 310 | 93 | 1006446 | 8 | 225 | 2921940 | 450 | 5843880 | 30 | 324660 | 18.2 | 196960.4 | 316 | 2 | 80 | 10822 | 175 | 10822 | 16 | 10822 | 96 | 0 | 300 | 0 | 4253046 | 365469762 | 393 | 33771
29 | Sahiwal-2nd | Ravi | Rural | 7589 | 245 | 73.5 | 557791.5 | 4 | 175.5 | 1598243.4 | 351 | 3196486.8 | 24 | 182136 | 22.12 | 167868.68 | 249 | 0 | 80 | 7589 | 175 | 7589 | 16 | 7589 | 96 | 0 | 300 | 0 | 2338170.9 | 203534703.3 | 308.1 | 26819.7
30 | Sahiwal-2nd | Jinnah Town | Rural | 6552 | 248 | 74.4 | 487468.8 | 8 | 181.6 | 1427811.84 | 363.2 | 2855623.68 | 29 | 190008 | 43.1 | 282391.2 | 256 | 0 | 80 | 6552 | 175 | 6552 | 16 | 6552 | 96 | 0 | 300 | 0 | 2105288.64 | 189743299.2 | 321.32 | 28959.6
31 | Sahiwal-2nd | Kool Wala | Rural | 2031 | 80 | 24 | 48744 | 4 | 60 | 146232 | 120 | 292464 | 10 | 20310 | 14.17 | 28779.27 | 84 | 0 | 80 | 2031 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 215286 | 19420828.2 | 106 | 9562.2
32 | Chichawatni | Firdous | Rural | 5728 | 178 | 53.4 | 305875.2 | 19 | 143.6 | 987048.96 | 287.2 | 1974097.92 | 168 | 962304 | 247 | 1414816 | 196 | 1 | 80 | 5728 | 175 | 5728 | 16 | 5728 | 96 | 5728 | 300 | 0 | 2255228.16 | 204252460.8 | 393.72 | 35658.6
33 | Chichawatni | Khalid Shaheed | Rural | 4915 | 94 | 28.2 | 138603 | 0 | 65.8 | 388088.4 | 131.6 | 776176.8 | 28 | 137620 | 127.55 | 626908.25 | 94 | 0 | 80 | 4915 | 175 | 0 | 16 | 4915 | 96 | 4915 | 300 | 0 | 664311.4 | 84600912 | 135.16 | 17212.8
34 | Chichawatni | Kot Muhammad | Rural | 4569 | 207 | 62.1 | 283734.9 | 21 | 165.9 | 909596.52 | 331.8 | 1819193.04 | 147 | 671643 | 201 | 918369 | 227 | 1 | 80 | 4569 | 175 | 4569 | 16 | 4569 | 96 | 4569 | 300 | 0 | 1864974.42 | 165104927.1 | 408.18 | 36135.9
35 | Chichawatni | Sheikh Tayyab | Rural | 7822 | 214 | 64.2 | 502172.4 | 12 | 161.8 | 1518719.52 | 323.6 | 3037439.04 | 102 | 797844 | 129 | 1009038 | 225 | 1 | 80 | 7822 | 175 | 7822 | 16 | 7822 | 96 | 7822 | 300 | 0 | 2818735.92 | 244295139.6 | 360.36 | 31231.8
36 | Chichawatni | Chichawatni Old | Rural | 10945 | 357 | 107.1 | 1172209.5 | 23 | 272.9 | 3584268.6 | 545.8 | 7168537.2 | 161 | 1762145 | 195 | 2134275 | 379 | 1 | 80 | 10945 | 175 | 10945 | 16 | 10945 | 96 | 10945 | 300 | 0 | 6518623.1 | 561685360.5 | 595.58 | 51318.9
37 | Chichawatni | Hazoor Abad | Rural | 6214 | 270 | 81 | 503334 | 24 | 213 | 1588298.4 | 426 | 3176596.8 | 191 | 1186874 | 226 | 1404364 | 293 | 1 | 80 | 6214 | 175 | 6214 | 16 | 6214 | 96 | 6214 | 300 | 0 | 3278506.4 | 276367650 | 527.6 | 44475
38 | Chichawatni | New Firdous | Rural | 6921 | 434 | 130.2 | 901114.2 | 1 | 304.8 | 2531424.96 | 609.6 | 5062849.92 | 31 | 214551 | 186 | 1287306 | 435 | 0 | 80 | 6921 | 175 | 6921 | 16 | 6921 | 96 | 6921 | 300 | 0 | 3647090.16 | 383712697.8 | 526.96 | 55441.8
39 | Chichawatni | Sher Wala | Rural | 4676 | 218 | 65.4 | 305810.4 | 12 | 164.6 | 923603.52 | 329.2 | 1847207.04 | 119 | 556444 | 134 | 626584 | 229 | 1 | 80 | 4676 | 175 | 4676 | 16 | 4676 | 96 | 4676 | 300 | 0 | 1785857.92 | 149344893.6 | 381.92 | 31938.6
40 | Chichawatni | Al-Noor | Rural | 3992 | 205 | 61.5 | 245508 | 7 | 150.5 | 720955.2 | 301 | 1441910.4 | 97 | 387224 | 122 | 487024 | 211 | 1 | 80 | 3992 | 175 | 3992 | 16 | 3992 | 96 | 3992 | 300 | 0 | 1353687.2 | 116472588 | 339.1 | 29176.5
41 | Chichawatni | New Sher Wala | Rural | 7815 | 697 | 209.1 | 1634116.5 | 2 | 489.9 | 4594282.2 | 979.8 | 9188564.4 | 15 | 117225 | 74.58 | 582842.7 | 699 | 0 | 80 | 7815 | 175 | 7815 | 16 | 0 | 96 | 0 | 300 | 0 | 6345623.7 | 591186775.5 | 811.98 | 75647.7
42 | Chichawatni | Ghazi | Rural | 5043 | 338 | 101.4 | 511360.2 | 3 | 239.6 | 1449963.36 | 479.2 | 2899926.72 | 35 | 176505 | 163.05 | 822261.15 | 341 | 0 | 80 | 5043 | 175 | 5043 | 16 | 5043 | 96 | 5043 | 300 | 0 | 2137828.56 | 224865352.8 | 423.92 | 44589.6
43 | Chichawatni | Ghazi Abad | Rural | 6954 | 344 | 103.2 | 717652.8 | 17 | 257.8 | 2151289.44 | 515.6 | 4302578.88 | 125 | 869250 | 147 | 1022238 | 360 | 1 | 80 | 6954 | 175 | 6954 | 16 | 6954 | 96 | 6954 | 300 | 0 | 3738192.24 | 321641971.2 | 537.56 | 46252.8
44 | Chichawatni | Shah Kot | Rural | 4714 | 276 | 82.8 | 390319.2 | 13 | 206.2 | 1166432.16 | 412.4 | 2332864.32 | 69 | 325266 | 94.2 | 444058.8 | 289 | 0 | 80 | 4714 | 175 | 4714 | 16 | 4714 | 96 | 0 | 300 | 0 | 1882017.36 | 167786344.8 | 399.24 | 35593.2
45 | Chichawatni | Kamal Shah | Rural | 2653 | 108 | 32.4 | 85957.2 | 6 | 81.6 | 259781.76 | 163.2 | 519563.52 | 36 | 95508 | 54.5 | 144588.5 | 114 | 0 | 80 | 2653 | 175 | 2653 | 16 | 2653 | 96 | 0 | 300 | 0 | 441246.96 | 40106992.8 | 166.32 | 15117.6
46 | Chichawatni | Mian Khera | Rural | 3416 | 201 | 60.3 | 205984.8 | 6 | 146.7 | 601352.64 | 293.4 | 1202705.28 | 36 | 122976 | 45.4 | 155086.4 | 207 | 0 | 80 | 3416 | 175 | 3416 | 16 | 3416 | 96 | 0 | 300 | 0 | 930313.44 | 82085455.2 | 272.34 | 24029.7
47 | Chichawatni | Kassowal | Rural | 4322 | 227 | 68.1 | 294328.2 | 16 | 174.9 | 907101.36 | 349.8 | 1814202.72 | 99 | 427878 | 162 | 700164 | 242 | 1 | 80 | 4322 | 175 | 4322 | 16 | 4322 | 96 | 4322 | 300 | 0 | 1629307.56 | 151744987.8 | 376.98 | 35109.9
48 | Chichawatni | Adeeb Shaheed | Rural | 381 | 48 | 14.4 | 5486.4 | 11 | 44.6 | 20391.12 | 89.2 | 40782.24 | 54 | 20574 | 102 | 38862 | 58 | 1 | 80 | 0 | 175 | 0 | 16 | 381 | 96 | 381 | 300 | 0 | 46451.52 | 4795113.6 | 121.92 | 12585.6
49 | Chichawatni | Chak 50 | Rural | 3516 | 158 | 47.4 | 166658.4 | 8 | 118.6 | 500397.12 | 237.2 | 1000794.24 | 24 | 84384 | 45.55 | 160153.8 | 166 | 0 | 80 | 3516 | 175 | 3516 | 16 | 3516 | 96 | 0 | 300 | 0 | 751439.52 | 70156857.6 | 213.72 | 19953.6
50 | Chichawatni | Daras Colony | Rural | 3305 | 126 | 37.8 | 124929 | 11 | 99.2 | 393427.2 | 198.4 | 786854.4 | 30 | 99150 | 58.55 | 193507.75 | 137 | 0 | 80 | 3305 | 175 | 3305 | 16 | 3305 | 96 | 0 | 300 | 0 | 617506.2 | 59196516 | 186.84 | 17911.2
51 | Chichawatni | Baba Khaki Shah | Rural | 4598 | 253 | 75.9 | 348988.2 | 6 | 183.1 | 1010272.56 | 366.2 | 2020545.12 | 48 | 220704 | 56.5 | 259787 | 259 | 0 | 80 | 4598 | 175 | 4598 | 16 | 4598 | 96 | 0 | 300 | 0 | 1579964.76 | 137866891.8 | 343.62 | 29984.1
52 | Chichawatni | Okanwala | Rural | 6874 | 202 | 60.6 | 416564.4 | 12 | 153.4 | 1265365.92 | 306.8 | 2530731.84 | 32 | 219968 | 33.5 | 230279 | 214 | 0 | 80 | 6874 | 175 | 6874 | 16 | 6874 | 96 | 0 | 300 | 0 | 1901898.32 | 166910343.6 | 276.68 | 24281.4
53 | Chichawatni | New Shah kot | Rural | 4667 | 325 | 97.5 | 455032.5 | 18 | 245.5 | 1374898.2 | 491 | 2749796.4 | 48 | 224016 | 55.5 | 259018.5 | 343 | 0 | 80 | 4667 | 175 | 4667 | 16 | 4667 | 96 | 0 | 300 | 0 | 2053946.7 | 181893991.5 | 440.1 | 38974.5
54 | Chichawatni | Harappa | Rural | 4817 | 92 | 27.6 | 132949.2 | 10 | 74.4 | 430061.76 | 148.8 | 860123.52 | 97 | 467249 | 120 | 578040 | 101 | 1 | 80 | 4817 | 175 | 4817 | 16 | 4817 | 96 | 4817 | 300 | 0 | 1030259.96 | 86688658.8 | 213.88 | 17996.4
55 | Chichawatni | Dad Fatiyana | Rural | 5587 | 187 | 56.1 | 313430.7 | 15 | 145.9 | 978171.96 | 291.8 | 1956343.92 | 131 | 731897 | 170 | 949790 | 201 | 1 | 80 | 5587 | 175 | 5587 | 16 | 5587 | 96 | 5587 | 300 | 0 | 2023499.66 | 175308327.3 | 362.18 | 31377.9
56 | Arif Wala | Jeven Shah | Rural | 5806 | 480 | 144 | 836064 | 37 | 373 | 2598765.6 | 746 | 5197531.2 | 129 | 748974 | 149.3 | 866835.8 | 517 | 0 | 80 | 5806 | 175 | 5806 | 16 | 5806 | 96 | 5806 | 300 | 0 | 4183803.6 | 366370212 | 720.6 | 63102
57 | Arif Wala | Old Factory | Rural | 3113 | 560 | 168 | 522984 | 40 | 432 | 1613779.2 | 864 | 3227558.4 | 110 | 342430 | 120.45 | 374960.85 | 600 | 0 | 80 | 3113 | 175 | 3113 | 16 | 3113 | 96 | 3113 | 300 | 0 | 2479193.2 | 217720107 | 796.4 | 69939
58 | Arif Wala | Gunj Shakar | Rural | 2447 | 80 | 24 | 58728 | 25 | 81 | 237848.4 | 162 | 475696.8 | 20 | 48940 | 14.2 | 34747.4 | 105 | 0 | 80 | 2447 | 175 | 2447 | 16 | 2447 | 96 | 0 | 300 | 0 | 345516.4 | 30802836 | 141.2 | 12588
59 | Arif Wala | Kalyana | Rural | 5193 | 490 | 147 | 763371 | 39 | 382 | 2380471.2 | 764 | 4760942.4 | 140 | 727020 | 136.25 | 707546.25 | 529 | 0 | 80 | 5193 | 175 | 5193 | 16 | 5193 | 96 | 5193 | 300 | 0 | 3870862.2 | 330399432 | 745.4 | 63624
60 | Arif Wala | Hotta | Rural | 3134 | 520 | 156 | 488904 | 36 | 400 | 1504320 | 800 | 3008640 | 110 | 344740 | 118.17 | 370344.78 | 556 | 0 | 80 | 3134 | 175 | 3134 | 16 | 3134 | 96 | 3134 | 300 | 0 | 2337964 | 204205798.8 | 746 | 65158.2
61 | Arif Wala | Baba Farid | Rural | 3238 | 517 | 155.1 | 502213.8 | 17 | 378.9 | 1472253.84 | 757.8 | 2944507.68 | 22 | 71236 | 34.5 | 111711 | 534 | 0 | 80 | 3238 | 175 | 3238 | 16 | 3238 | 96 | 0 | 300 | 0 | 2045703.64 | 184879762.2 | 631.78 | 57096.9
62 | Arif Wala | Irshaad Dastagir | Rural | 5073 | 349 | 104.7 | 531143.1 | 13 | 257.3 | 1566339.48 | 514.6 | 3132678.96 | 38 | 192774 | 42 | 213066 | 362 | 0 | 80 | 5073 | 175 | 5073 | 16 | 5073 | 96 | 0 | 300 | 0 | 2290256.58 | 202338126.9 | 451.46 | 39885.3
63 | Arif Wala | Hotta City | Rural | 3223 | 520 | 156 | 502788 | 3 | 367 | 1419409.2 | 734 | 2838818.4 | 26 | 83798 | 32.38 | 104360.74 | 523 | 0 | 80 | 3223 | 175 | 3223 | 16 | 3223 | 96 | 0 | 300 | 0 | 2005995.2 | 178099112.4 | 622.4 | 55258.8
64 | Arif Wala | Zafar Shaheed | Rural | 2713 | 416 | 124.8 | 338582.4 | 7 | 298.2 | 970819.92 | 596.4 | 1941639.84 | 32 | 86816 | 38 | 103094 | 423 | 0 | 80 | 2713 | 175 | 2713 | 16 | 2713 | 96 | 0 | 300 | 0 | 1396218.32 | 123699777.6 | 514.64 | 45595.2
65 | Arif Wala | Karmanwala | Rural | 3889 | 536 | 160.8 | 625351.2 | 38 | 413.2 | 1928321.76 | 826.4 | 3856643.52 | 130 | 505570 | 145.4 | 565460.6 | 574 | 0 | 80 | 3889 | 175 | 3889 | 16 | 3889 | 96 | 3889 | 300 | 0 | 3059242.96 | 267202300.8 | 786.64 | 68707.2
66 | Arif Wala | Nawabanwala | Rural | 3859 | 490 | 147 | 567273 | 28 | 371 | 1718026.8 | 742 | 3436053.6 | 116 | 447644 | 117.2 | 452274.8 | 518 | 0 | 80 | 3859 | 175 | 3859 | 16 | 3859 | 96 | 3859 | 300 | 0 | 2732943.8 | 235001523 | 708.2 | 60897
67 | Arif Wala | Al-Madni | Rural | 3544 | 610 | 183 | 648552 | 32 | 459 | 1952035.2 | 918 | 3904070.4 | 129 | 457176 | 133.15 | 471883.6 | 642 | 0 | 80 | 3544 | 175 | 3544 | 16 | 3544 | 96 | 3544 | 300 | 0 | 3057763.2 | 264502896 | 862.8 | 74634
68 | Arif Wala | Tirikhni Road | Rural | 5563 | 530 | 159 | 884517 | 36 | 407 | 2716969.2 | 814 | 5433938.4 | 110 | 611930 | 103.12 | 573656.56 | 565 | 1 | 80 | 5563 | 175 | 5563 | 16 | 5563 | 96 | 5563 | 300 | 0 | 4213416.2 | 363109248.6 | 757.4 | 65272.2
69 | Arif Wala | Qalandar Shah | Rural | 4413 | 470 | 141 | 622233 | 33 | 362 | 1917007.2 | 724 | 3834014.4 | 108 | 476604 | 90.46 | 399199.98 | 503 | 0 | 80 | 4413 | 175 | 4413 | 16 | 4413 | 96 | 0 | 300 | 0 | 3015844.2 | 255859561.8 | 683.4 | 57978.6
70 | Arif Wala | New Factory | Rural | 5163 | 510 | 153 | 789939 | 36 | 393 | 2434870.8 | 786 | 4869741.6 | 106 | 547278 | 110.2 | 568962.6 | 546 | 0 | 80 | 5163 | 175 | 5163 | 16 | 5163 | 96 | 5163 | 300 | 0 | 3772087.8 | 328692069 | 730.6 | 63663
71 | Arif Wala | Yusaf Steel/Peer Fazal Chishti | Rural | 2434 | 610 | 183 | 445422 | 12 | 439 | 1282231.2 | 878 | 2564462.4 | 4 | 9736 | 2.15 | 5233.1 | 622 | 0 | 80 | 2434 | 175 | 2434 | 16 | 0 | 96 | 0 | 300 | 0 | 1737389.2 | 155517996 | 713.8 | 63894
72 | Arif Wala | Chak:67 | Rural | 3593 | 460 | 138 | 495834 | 38 | 360 | 1552176 | 720 | 3104352 | 90 | 323370 | 75.4 | 270912.2 | 498 | 0 | 80 | 3593 | 175 | 3593 | 16 | 3593 | 96 | 0 | 300 | 0 | 2371380 | 204003354 | 660 | 56778
73 | Arif Wala | Arif Shaheed | Rural | 2754 | 480 | 144 | 396576 | 35 | 371 | 1226080.8 | 742 | 2452161.6 | 5 | 13770 | 102.27 | 281651.58 | 515 | 0 | 80 | 2754 | 175 | 2754 | 16 | 0 | 96 | 2754 | 300 | 0 | 1636426.8 | 165218518.8 | 594.2 | 59992.2
74 | Arif Wala | Burewala Road | Rural | 4628 | 560 | 168 | 777504 | 40 | 432 | 2399155.2 | 864 | 4798310.4 | 126 | 583128 | 124.16 | 574612.48 | 600 | 0 | 80 | 4628 | 175 | 4628 | 16 | 4628 | 96 | 4628 | 300 | 0 | 3759787.2 | 324707884.8 | 812.4 | 70161.6
75 | Arif Wala | Ch. Naseem | Rural | 2964 | 631 | 189.3 | 561085.2 | 14 | 455.7 | 1620833.76 | 911.4 | 3241667.52 | 7 | 20748 | 7.1 | 21044.4 | 645 | 0 | 80 | 2964 | 175 | 2964 | 16 | 0 | 96 | 0 | 300 | 0 | 2202666.96 | 197445970.8 | 743.14 | 66614.7
76 | Arif Wala | Chak 117/EB | Rural | 2780 | 596 | 178.8 | 497064 | 12 | 429.2 | 1431811.2 | 858.4 | 2863622.4 | 35 | 97300 | 35.15 | 97717 | 608 | 0 | 80 | 2780 | 175 | 2780 | 16 | 2780 | 96 | 0 | 300 | 0 | 2026175.2 | 179171556 | 728.84 | 64450.2
77 | Arif Wala | Moj Darya | Rural | 4688 | 658 | 197.4 | 925411.2 | 6 | 466.6 | 2624904.96 | 933.2 | 5249809.92 | 3 | 14064 | 2.45 | 11485.6 | 664 | 0 | 80 | 4688 | 175 | 4688 | 16 | 0 | 96 | 0 | 300 | 0 | 3564380.16 | 318453964.8 | 760.32 | 67929.6
78 | Arif Wala | Mehdi Khan | Rural | 4535 | 713 | 213.9 | 970036.5 | 13 | 512.1 | 2786848.2 | 1024.2 | 5573696.4 | 4 | 18140 | 19.1 | 86618.5 | 726 | 0 | 80 | 4535 | 175 | 4535 | 16 | 0 | 96 | 0 | 300 | 0 | 3775024.7 | 342529003.5 | 832.42 | 75530.1
79 | Arif Wala | Sheher Jillani | Rural | 3046 | 675 | 202.5 | 616815 | 14 | 486.5 | 1778254.8 | 973 | 3556509.6 | 7 | 21322 | 17.35 | 52848.1 | 689 | 0 | 80 | 3046 | 175 | 3046 | 16 | 0 | 96 | 0 | 300 | 0 | 2416391.8 | 218411907 | 793.3 | 71704.5
80 | Arif Wala | Mohsin Shah | Rural | 2289 | 616 | 184.8 | 423007.2 | 7 | 438.2 | 1203647.76 | 876.4 | 2407295.52 | 24 | 54936 | 43.4 | 99342.6 | 623 | 0 | 80 | 2289 | 175 | 2289 | 16 | 2289 | 96 | 0 | 300 | 0 | 1681590.96 | 151667308.8 | 734.64 | 66259.2
81 | Arif Wala | Diwan Dastgeer | Rural | 3519 | 601 | 180.3 | 634475.7 | 11 | 431.7 | 1822982.76 | 863.4 | 3645965.52 | 21 | 73899 | 47.3 | 166448.7 | 612 | 0 | 80 | 3519 | 175 | 3519 | 16 | 3519 | 96 | 0 | 300 | 0 | 2531357.46 | 230648280.3 | 719.34 | 65543.7
82 | Arif Wala | Magghar | Rural | 5684 | 590 | 177 | 1006068 | 39 | 452 | 3083001.6 | 904 | 6166003.2 | 121 | 687764 | 98.4 | 559305.6 | 629 | 0 | 80 | 5684 | 175 | 5684 | 16 | 5684 | 96 | 5684 | 300 | 0 | 4776833.6 | 406536732 | 840.4 | 71523
83 | Arif Wala | Ghulam Qadir | Rural | 3367 | 487 | 146.1 | 491918.7 | 32 | 372.9 | 1506665.16 | 745.8 | 3013330.32 | 102 | 343434 | 75.22 | 253265.74 | 519 | 0 | 80 | 3367 | 175 | 3367 | 16 | 3367 | 96 | 0 | 300 | 0 | 2342017.86 | 197471519.7 | 695.58 | 58649.1
84 | Arif Wala | Qaboola | Rural | 2904 | 496 | 148.8 | 432115.2 | 31 | 378.2 | 1317951.36 | 756.4 | 2635902.72 | 110 | 319440 | 97.2 | 282268.8 | 527 | 0 | 80 | 2904 | 175 | 2904 | 16 | 2904 | 96 | 2904 | 300 | 0 | 2069506.56 | 176386636.8 | 712.64 | 60739.2
85 | Arif Wala | Irshad Shah | Rural | 6773 | 590 | 177 | 1198821 | 29 | 442 | 3592399.2 | 884 | 7184798.4 | 125 | 846625 | 104.15 | 705407.95 | 619 | 0 | 80 | 6773 | 175 | 6773 | 16 | 6773 | 96 | 6773 | 300 | 0 | 5637845.2 | 477008844 | 832.4 | 70428
86 | Arif Wala | Lal Shah | Rural | 3980 | 652 | 195.6 | 778488 | 12 | 468.4 | 2237078.4 | 936.8 | 4474156.8 | 35 | 139300 | 35.15 | 139897 | 664 | 0 | 80 | 3980 | 175 | 3980 | 16 | 3980 | 96 | 0 | 300 | 0 | 3154866.4 | 279178692 | 792.68 | 70145.4
87 | Arif Wala | Muhammad Nagar | Rural | 4457 | 754 | 226.2 | 1008173.4 | 18 | 545.8 | 2919156.72 | 1091.6 | 5838313.44 | 12 | 53484 | 20.4 | 90922.8 | 772 | 0 | 80 | 4457 | 175 | 4457 | 16 | 0 | 96 | 0 | 300 | 0 | 3980814.12 | 358778694.6 | 893.16 | 80497.8
88 | Arif Wala | Jamman Shah | Rural | 1873 | 653 | 195.9 | 366920.7 | 11 | 468.1 | 1052101.56 | 936.2 | 2104203.12 | 12 | 22476 | 18.13 | 33957.49 | 664 | 0 | 80 | 1873 | 175 | 1873 | 16 | 0 | 96 | 0 | 300 | 0 | 1441498.26 | 129390398.7 | 769.62 | 69081.9
89 | Arif Wala | Ahmed Yar | Rural | 5955 | 625 | 187.5 | 1116562.5 | 16 | 453.5 | 3240711 | 907 | 6481422 | 15 | 89325 | 25.15 | 149768.25 | 641 | 0 | 80 | 5955 | 175 | 5955 | 16 | 0 | 96 | 0 | 300 | 0 | 4446598.5 | 401221102.5 | 746.7 | 67375.5
90 | Arif Wala | Aslam Shaheed | Rural | 2410 | 699 | 209.7 | 505377 | 12 | 501.3 | 1449759.6 | 1002.6 | 2899519.2 | 25 | 60250 | 29.1 | 70131 | 711 | 0 | 80 | 2410 | 175 | 2410 | 16 | 2410 | 96 | 0 | 300 | 0 | 2015386.6 | 179695143 | 836.26 | 74562.3
91 | Arif Wala | Raja Fida Hussain | Rural | 3545 | 760 | 228 | 808260 | 14 | 546 | 2322684 | 1092 | 4645368 | 18 | 63810 | 22.1 | 78344.5 | 774 | 0 | 80 | 3545 | 175 | 3545 | 16 | 3545 | 96 | 0 | 300 | 0 | 3194754 | 285847530 | 901.2 | 80634
92 | Arif Wala | Kameer City | Rural | 8990 | 330 | 99 | 890010 | 14 | 245 | 2643060 | 490 | 5286120 | 25 | 224750 | 56.22 | 505417.8 | 344 | 0 | 80 | 8990 | 175 | 8990 | 16 | 8990 | 96 | 0 | 300 | 0 | 3757820 | 350162298 | 418 | 38950.2
93 | Arif Wala | Baba Qutab Shah | Rural | 6326 | 258 | 77.4 | 489632.4 | 7 | 187.6 | 1424109.12 | 375.2 | 2848218.24 | 12 | 75912 | 24.12 | 152583.12 | 265 | 0 | 80 | 6326 | 175 | 6326 | 16 | 0 | 96 | 0 | 300 | 0 | 1989653.52 | 181516978.8 | 314.52 | 28693.8
94 | Arif Wala | Pakpattan Road | Rural | 4322 | 363 | 108.9 | 470665.8 | 10 | 264.1 | 1369728.24 | 528.2 | 2739456.48 | 23 | 99406 | 31.42 | 135797.24 | 373 | 0 | 80 | 4322 | 175 | 4322 | 16 | 4322 | 96 | 0 | 300 | 0 | 1939800.04 | 173927220.6 | 448.82 | 40242.3
95 | Arif Wala | Rang Shah | Rural | 4148 | 540 | 162 | 671976 | 28 | 406 | 2020905.6 | 812 | 4041811.2 | 88 | 365024 | 56.27 | 233407.96 | 568 | 0 | 80 | 4148 | 175 | 4148 | 16 | 4148 | 96 | 0 | 300 | 0 | 3057905.6 | 258529077.6 | 737.2 | 62326.2
96 | Arif Wala | Muhammad Panah | Rural | 1472 | 470 | 141 | 207552 | 26 | 355 | 627072 | 710 | 1254144 | 80 | 117760 | 60.35 | 88835.2 | 496 | 0 | 80 | 1472 | 175 | 1472 | 16 | 1472 | 96 | 0 | 300 | 0 | 952384 | 81201408 | 647 | 55164
97 | Pakpattan | Chak Baidi | Rural | 3402 | 399 | 119.7 | 407219.4 | 11 | 290.3 | 1185120.72 | 580.6 | 2370241.44 | 252 | 857304 | 287.6 | 978415.2 | 409 | 1 | 80 | 3402 | 175 | 3402 | 16 | 3402 | 96 | 3402 | 300 | 0 | 2449644.12 | 202141056.6 | 720.06 | 59418.3
98 | Pakpattan | Farid Kot | Rural | 4011 | 230 | 69 | 276759 | 0.4 | 161.4 | 776850.48 | 322.8 | 1553700.96 | 221 | 886431 | 209.02 | 838379.22 | 228 | 2 | 80 | 4011 | 175 | 4011 | 16 | 4011 | 96 | 4011 | 300 | 0 | 1940040.48 | 144355087.8 | 483.68 | 35989.8
99 | Pakpattan | Al-Wardi | Rural | 4172 | 308 | 92.4 | 385492.8 | 15 | 230.6 | 1154475.84 | 461.2 | 2308951.68 | 11 | 45892 | 70.4 | 293708.8 | 321 | 2 | 80 | 4172 | 175 | 4172 | 16 | 0 | 96 | 0 | 300 | 0 | 1585860.64 | 157316107.2 | 380.12 | 37707.6
100 | Pakpattan | Ghazi Mardan | Rural | 5464 | 403 | 120.9 | 660597.6 | 12 | 294.1 | 1928354.88 | 588.2 | 3856709.76 | 25 | 136600 | 122.2 | 667700.8 | 414 | 1 | 80 | 5464 | 175 | 5464 | 16 | 5464 | 96 | 5464 | 300 | 0 | 2725552.48 | 273446426.4 | 498.82 | 50045.1
101 | Pakpattan | Sikandar Chowk | Rural | 4019 | 311 | 93.3 | 374972.7 | 10 | 227.7 | 1098151.56 | 455.4 | 2196303.12 | 10 | 40190 | 54.1 | 217427.9 | 320 | 1 | 80 | 4019 | 175 | 4019 | 16 | 0 | 96 | 0 | 300 | 0 | 1513314.26 | 145948779.3 | 376.54 | 36314.7
102 | Pakpattan | Qudrat Ullah | Rural | 4866 | 378 | 113.4 | 551804.4 | 13 | 277.6 | 1620961.92 | 555.2 | 3241923.84 | 14 | 68124 | 42.15 | 205101.9 | 390 | 1 | 80 | 4866 | 175 | 4866 | 16 | 0 | 96 | 0 | 300 | 0 | 2240890.32 | 208476957.6 | 460.52 | 42843.6
103 | Pakpattan | Noor pur | Rural | 3479 | 641 | 192.3 | 669011.7 | 22 | 470.7 | 1965078.36 | 941.4 | 3930156.72 | 33 | 114807 | 50.25 | 174819.75 | 663 | 0 | 80 | 3479 | 175 | 3479 | 16 | 3479 | 96 | 0 | 300 | 0 | 2748897.06 | 248305623.3 | 790.14 | 71372.7
104 | Pakpattan | Jafar Shah | Rural | 2616 | 612 | 183.6 | 480297.6 | 24 | 452.4 | 1420174.08 | 904.8 | 2840348.16 | 30 | 78480 | 51.08 | 133625.28 | 636 | 0 | 80 | 2616 | 175 | 2616 | 16 | 2616 | 96 | 0 | 300 | 0 | 1978951.68 | 179879299.2 | 756.48 | 68761.2
105 | Pakpattan | Hurry Pur | Rural | 5792 | 444 | 133.2 | 771494.4 | 22 | 332.8 | 2313093.12 | 665.6 | 4626186.24 | 48 | 278016 | 65.39 | 378738.88 | 466 | 0 | 80 | 5792 | 175 | 5792 | 16 | 5792 | 96 | 0 | 300 | 0 | 3362603.52 | 302609990.4 | 580.56 | 52246.2
106 | Pakpattan | Noor Jhang | Rural | 3712 | 471 | 141.3 | 524505.6 | 25 | 354.7 | 1579975.68 | 709.4 | 3159951.36 | 47 | 174464 | 57.03 | 211695.36 | 496 | 0 | 80 | 3712 | 175 | 3712 | 16 | 3712 | 96 | 0 | 300 | 0 | 2278945.28 | 203872320 | 613.94 | 54922.5
107 | Pakpattan | Jahan Khan | Rural | 4876 | 834 | 250.2 | 1219975.2 | 38 | 621.8 | 3638276.16 | 1243.6 | 7276552.32 | 27 | 131652 | 37.37 | 182216.12 | 872 | 0 | 80 | 4876 | 175 | 4876 | 16 | 4876 | 96 | 0 | 300 | 0 | 4989903.36 | 451186032 | 1023.36 | 92532
108 | Pakpattan | Waris Shah | Rural | 3654 | 714 | 214.2 | 782686.8 | 51 | 550.8 | 2415147.84 | 1101.6 | 4830295.68 | 36 | 131544 | 54.59 | 199471.86 | 765 | 0 | 80 | 3654 | 175 | 3654 | 16 | 3654 | 96 | 0 | 300 | 0 | 3329378.64 | 304134112.8 | 911.16 | 83233.2
109 | Pakpattan | Al-Noor | Rural | 3007 | 296 | 88.8 | 267021.6 | 7 | 214.2 | 772919.28 | 428.4 | 1545838.56 | 6 | 18042 | 13 | 39091 | 303 | 0 | 80 | 3007 | 175 | 3007 | 16 | 0 | 96 | 0 | 300 | 0 | 1057982.88 | 95896838.4 | 351.84 | 31891.2
110 | Pakpattan | Bias | Rural | 2411 | 580 | 174 | 419514 | 37 | 443 | 1281687.6 | 886 | 2563375.2 | 42 | 101262 | 96.37 | 232348.07 | 616 | 0 | 80 | 2411 | 175 | 2411 | 16 | 2411 | 96 | 2411 | 300 | 0 | 1802463.6 | 169001938.2 | 747.6 | 70096.2
111 | Pakpattan | Chak Ghurri | Rural | 3258 | 671 | 201.3 | 655835.4 | 32 | 501.7 | 1961446.32 | 1003.4 | 3922892.64 | 146 | 475668 | 97.09 | 316319.22 | 701 | 0 | 80 | 3258 | 175 | 3258 | 16 | 3258 | 96 | 3258 | 300 | 0 | 3092949.72 | 256320217.8 | 949.34 | 78674.1
112 | Pakpattan | Ghulam Haidar | Rural | 2245 | 406 | 121.8 | 273441 | 18 | 302.2 | 814126.8 | 604.4 | 1628253.6 | 88 | 197560 | 233.45 | 524095.25 | 421 | 0 | 80 | 2245 | 175 | 2245 | 16 | 2245 | 96 | 2245 | 300 | 0 | 1285127.8 | 129961254 | 572.44 | 57889.2
113 | Pakpattan | Malka Hans | Rural | 3377 | 487 | 146.1 | 493379.7 | 30 | 370.9 | 1503035.16 | 741.8 | 3006070.32 | 76 | 256652 | 186.3 | 629135.1 | 414 | 0 | 80 | 3377 | 175 | 3377 | 16 | 3377 | 96 | 3377 | 300 | 0 | 2253066.86 | 219592464.3 | 667.18 | 65025.9
114 | Pakpattan | New Malka Hans | Rural | 1692 | 407 | 122.1 | 206593.2 | 26 | 310.9 | 631251.36 | 621.8 | 1262502.72 | 68 | 115056 | 150.15 | 254053.8 | 428 | 0 | 80 | 1692 | 175 | 1692 | 16 | 1692 | 96 | 1692 | 300 | 0 | 952900.56 | 91613170.8 | 563.18 | 54144.9
115 | Pakpattan | Sanday Khan | Rural | 3338 | 431 | 129.3 | 431603.4 | 20 | 321.7 | 1288601.52 | 643.4 | 2577203.04 | 91 | 303758 | 257.35 | 859034.3 | 445 | 0 | 80 | 3338 | 175 | 3338 | 16 | 3338 | 96 | 3338 | 300 | 0 | 2023962.92 | 207469050.6 | 606.34 | 62153.7
116 | Pakpattan | Mehboob Shah | Rural | 2520 | 347 | 104.1 | 262332 | 18 | 260.9 | 788961.6 | 521.8 | 1577923.2 | 92 | 231840 | 143 | 360360 | 358 | 0 | 80 | 2520 | 175 | 2520 | 16 | 2520 | 96 | 2520 | 300 | 0 | 1283133.6 | 117083988 | 509.18 | 46461.9
117 | Pakpattan | Miran Shah | Rural | 5299 | 480 | 144 | 763056 | 15 | 351 | 2231938.8 | 702 | 4463877.6 | 92 | 487508 | 312.43 | 1655566.57 | 495 | 0 | 80 | 5299 | 175 | 5299 | 16 | 5299 | 96 | 5299 | 300 | 0 | 3482502.8 | 369455818.2 | 657.2 | 69721.8
118 | Pakpattan | Sarwar Shaheed | Rural | 2056 | 310 | 93 | 191208 | 20 | 237 | 584726.4 | 474 | 1169452.8 | 58 | 119248 | 123.45 | 253813.2 | 330 | 0 | 80 | 2056 | 175 | 2056 | 16 | 2056 | 96 | 2056 | 300 | 0 | 895182.4 | 85969584 | 435.4 | 41814
119 | Pakpattan | Masoom shah | Rural | 2646 | 410 | 123 | 325458 | 11 | 298 | 946209.6 | 596 | 1892419.2 | 83 | 219618 | 223 | 590058 | 421 | 0 | 80 | 2646 | 175 | 2646 | 16 | 2646 | 96 | 2646 | 300 | 0 | 1491285.6 | 149925006 | 563.6 | 56661
120 | Pakpattan | Gunj Shakar | Rural | 2277 | 521 | 156.3 | 355895.1 | 26 | 390.7 | 1067548.68 | 781.4 | 2135097.36 | 77 | 175329 | 236 | 537372 | 547 | 0 | 80 | 2277 | 175 | 2277 | 16 | 2277 | 96 | 2277 | 300 | 0 | 1598772.78 | 161415846.9 | 702.14 | 70889.7
121 | Pakpattan | Bonga Hyat | Rural | 5459 | 515 | 154.5 | 843415.5 | 9 | 369.5 | 2420520.6 | 739 | 4841041.2 | 72 | 393048 | 285.43 | 1558162.37 | 524 | 0 | 80 | 5459 | 175 | 5459 | 16 | 5459 | 96 | 5459 | 300 | 0 | 3656984.1 | 386482460.7 | 669.9 | 70797.3
122 | Pakpattan | Hussainabad | Rural | 4206 | 489 | 146.7 | 617020.2 | 14 | 356.3 | 1798317.36 | 712.6 | 3596634.72 | 86 | 361716 | 212.05 | 891882.3 | 503 | 0 | 80 | 4206 | 175 | 4206 | 16 | 4206 | 96 | 4206 | 300 | 0 | 2777053.56 | 271162081.8 | 660.26 | 64470.3
123 | Pakpattan | Satluj | Rural | 3944 | 491 | 147.3 | 580951.2 | 12 | 355.7 | 1683456.96 | 711.4 | 3366913.92 | 97 | 382568 | 321.35 | 1267404.4 | 503 | 0 | 80 | 3944 | 175 | 3944 | 16 | 3944 | 96 | 3944 | 300 | 0 | 2646976.16 | 279801952.8 | 671.14 | 70943.7
124 | Pakpattan | Iqbal Shaheed | Rural | 3530 | 397 | 119.1 | 420423 | 23 | 300.9 | 1274612.4 | 601.8 | 2549224.8 | 97 | 342410 | 357.4 | 1261622 | 420 | 0 | 80 | 3530 | 175 | 3530 | 16 | 3530 | 96 | 3530 | 300 | 0 | 2037445.4 | 229912077 | 577.18 | 65130.9
125 | Pakpattan | Chak Shafi | Rural | 3561 | 471 | 141.3 | 503169.3 | 14 | 343.7 | 1468698.84 | 687.4 | 2937397.68 | 53 | 188733 | 133.35 | 474859.35 | 485 | 0 | 80 | 3561 | 175 | 3561 | 16 | 3561 | 96 | 3561 | 300 | 0 | 2160601.14 | 206244929.7 | 606.74 | 57917.7
126 | Pakpattan | Chan Peer | Rural | 5888 | 587 | 176.1 | 1036876.8 | 21 | 431.9 | 3051632.64 | 863.8 | 6103265.28 | 117 | 688896 | 409.05 | 2408486.4 | 608 | 0 | 80 | 5888 | 175 | 5888 | 16 | 5888 | 96 | 5888 | 300 | 0 | 4777405.44 | 513815731.2 | 811.38 | 87264.9
127 | Pakpattan | Baba Abdul Karim | Rural | 1971 | 376 | 112.8 | 222328.8 | 13 | 276.2 | 653268.24 | 552.4 | 1306536.48 | 60 | 118260 | 139.43 | 274816.53 | 389 | 0 | 80 | 1971 | 175 | 1971 | 16 | 1971 | 96 | 1971 | 300 | 0 | 993857.04 | 95548167 | 504.24 | 48477
128 | Pakpattan | Karmanwala | Rural | 3699 | 45 | 13.5 | 49936.5 | 11 | 42.5 | 188649 | 85 | 377298 | 12 | 44388 | 24.29 | 89848.71 | 56 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 282973.5 | 28178612.1 | 76.5 | 7617.9
|  | TOTAL |  | 525289 | 40604 | 12945.3 | 61075507.8 | 2251.4 | 32644.1 | 185943324.72 | 65288.2 | 371886649.44 | 4959 | 32335909 | 8625.37 | 43825836.3 | 45565 | 24 | 80 | 524908 | 175 | 517962 | 16 | 423934 | 96 | 200616 | 300 | 0 | 279354741.52 | 25125975667.8 | 531.8115 | 47832.6705

## 400-220 (Rural) RYKhan
Statement of 400/220 V MEPCO Consumers For 2020-21
R.Y Khan Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | R.Y.Khan | Palace | Rural | 4342 | 65 | 19.5 | 84669 | 35 | 80.5 | 419437.2 | 161 | 838874.4 | 3 | 13026 | 12 | 52104 | 100 | 0 | 80 | 4342 | 175 | 4342 | 16 | 0 | 96 | 0 | 300 | 0 | 517132.2 | 53712711 | 119.1 | 12370.5
2 | R.Y.Khan | Scarp-3 | Rural | 5734 | 80 | 24 | 137616 | 55 | 111 | 763768.8 | 222 | 1527537.6 | 3 | 17202 | 8 | 45872 | 135 | 0 | 80 | 5734 | 175 | 5734 | 16 | 0 | 96 | 0 | 300 | 0 | 918586.8 | 94817424 | 160.2 | 16536
3 | R.Y.Khan | Hussain Abad | Rural | 9665 | 58 | 17.4 | 168171 | 35 | 75.6 | 876808.8 | 151.2 | 1753617.6 | 4 | 38660 | 15 | 144975 | 93 | 0 | 80 | 9665 | 175 | 9665 | 16 | 0 | 96 | 0 | 300 | 0 | 1083639.8 | 114420069 | 112.12 | 11838.6
4 | R.Y.Khan | Al-Khair | Rural | 148 | 15 | 4.5 | 666 | 4 | 14.5 | 2575.2 | 29 | 5150.4 | 5 | 740 | 15 | 2220 | 19 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 3981.2 | 444222 | 26.9 | 3001.5
5 | R.Y.Khan | Rohi | Rural | 6664 | 121 | 36.3 | 241903.2 | 60 | 144.7 | 1157136.96 | 289.4 | 2314273.92 | 8 | 53312 | 35 | 233240 | 181 | 0 | 80 | 6664 | 175 | 6664 | 16 | 0 | 96 | 0 | 300 | 0 | 1452352.16 | 153576544.8 | 217.94 | 23045.7
6 | R.Y.Khan | Taranda | Rural | 6057 | 65 | 19.5 | 118111.5 | 21 | 66.5 | 483348.6 | 133 | 966697.2 | 11 | 66627 | 65 | 393705 | 86 | 0 | 80 | 6057 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 668087.1 | 81978466.5 | 110.3 | 13534.5
7 | R.Y.Khan | Scarp-10 | Rural | 754 | 19 | 5.7 | 4297.8 | 4 | 17.3 | 15653.04 | 34.6 | 31306.08 | 4 | 3016 | 12 | 9048 | 23 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 22966.84 | 2434138.2 | 30.46 | 3228.3
8 | R.Y.Khan | Rehman Pur | Rural | 8157 | 140 | 42 | 342594 | 75 | 173 | 1693393.2 | 346 | 3386786.4 | 15 | 122355 | 60 | 489420 | 215 | 0 | 80 | 8157 | 175 | 8157 | 16 | 0 | 96 | 0 | 300 | 0 | 2158342.2 | 233600166 | 264.6 | 28638
9 | R.Y.Khan | Sultan Pur | Rural | 5635 | 125 | 37.5 | 211312.5 | 21 | 108.5 | 733677 | 217 | 1467354 | 15 | 84525 | 60 | 338100 | 146 | 0 | 80 | 5635 | 175 | 5635 | 16 | 0 | 96 | 0 | 300 | 0 | 1029514.5 | 108961177.5 | 182.7 | 19336.5
10 | R.Y.Khan | Scarp-08 | Rural | 5924 | 112 | 33.6 | 199046.4 | 35 | 113.4 | 806137.92 | 226.8 | 1612275.84 | 15 | 88860 | 60 | 355440 | 147 | 0 | 80 | 5924 | 175 | 5924 | 16 | 0 | 96 | 0 | 300 | 0 | 1094044.32 | 118660089.6 | 184.68 | 20030.4
11 | R.Y.Khan | Scarp-09 | Rural | 8263 | 99 | 29.7 | 245411.1 | 33 | 102.3 | 1014365.88 | 204.6 | 2028731.76 | 18 | 148734 | 75 | 619725 | 132 | 0 | 80 | 8263 | 175 | 8263 | 16 | 8263 | 96 | 0 | 300 | 0 | 1408510.98 | 159643638.9 | 170.46 | 19320.3
12 | R.Y.Khan | Shah Garh | Rural | 7681 | 98 | 29.4 | 225821.4 | 27 | 95.6 | 881164.32 | 191.2 | 1762328.64 | 240 | 1843440 | 250 | 1920250 | 125 | 0 | 80 | 7681 | 175 | 7681 | 16 | 7681 | 96 | 7681 | 300 | 0 | 2950425.72 | 221632182.6 | 384.12 | 28854.6
13 | R.Y.Khan | Aab-e-Hayat | Rural | 3490 | 51 | 15.3 | 53397 | 15 | 50.7 | 212331.6 | 101.4 | 424663.2 | 18 | 62820 | 25 | 87250 | 66 | 0 | 80 | 0 | 175 | 0 | 16 | 3490 | 96 | 0 | 300 | 0 | 328548.6 | 30874983 | 94.14 | 8846.7
14 | R.Y.Khan | Bahadur Pur (T/Well) | Rural | 6813 | 52 | 15.6 | 106282.8 | 24 | 60.4 | 493806.24 | 120.8 | 987612.48 | 4 | 27252 | 28 | 190764 | 76 | 0 | 80 | 6813 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 627341.04 | 71021437.2 | 92.08 | 10424.4
15 | R.Y.Khan | Sheikh Wahan | Rural | 5415 | 41 | 12.3 | 66604.5 | 18 | 46.7 | 303456.6 | 93.4 | 606913.2 | 4 | 21660 | 12 | 64980 | 59 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 391721.1 | 40513405.5 | 72.34 | 7481.7
16 | R.Y.Khan | NMC-1 | Rural | 3343 | 100 | 30 | 100290 | 21 | 91 | 365055.6 | 182 | 730111.2 | 4 | 13372 | 12 | 40116 | 121 | 0 | 80 | 3343 | 175 | 3343 | 16 | 0 | 96 | 0 | 300 | 0 | 478717.6 | 46514502 | 143.2 | 13914
17 | R.Y.Khan | Scarp-02 | Rural | 5721 | 98 | 29.4 | 168197.4 | 12 | 80.6 | 553335.12 | 161.2 | 1106670.24 | 4 | 22884 | 20 | 114420 | 110 | 0 | 80 | 5721 | 175 | 5721 | 16 | 0 | 96 | 0 | 300 | 0 | 744416.52 | 73770006.6 | 130.12 | 12894.6
18 | R.Y.Khan | Scarp-04 | Rural | 1302 | 40 | 12 | 15624 | 15 | 43 | 67183.2 | 86 | 134366.4 | 4 | 5208 | 20 | 26040 | 55 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 88015.2 | 9671256 | 67.6 | 7428
19 | R.Y.Khan | Iqbal Abad | Rural | 5750 | 140 | 42 | 241500 | 48 | 146 | 1007400 | 292 | 2014800 | 4 | 23000 | 20 | 115000 | 188 | 0 | 80 | 5750 | 175 | 5750 | 16 | 0 | 96 | 0 | 300 | 0 | 1271900 | 128512500 | 221.2 | 22350
20 | R.Y.Khan | Muslim Chowk | Rural | 536 | 28 | 8.4 | 4502.4 | 12 | 31.6 | 20325.12 | 63.2 | 40650.24 | 4 | 2144 | 16 | 8576 | 40 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 26971.52 | 2967081.6 | 50.32 | 5535.6
21 | R.Y.Khan | Colony | Rural | 3498 | 32 | 9.6 | 33580.8 | 9 | 31.4 | 131804.64 | 62.8 | 263609.28 | 4 | 13992 | 16 | 55968 | 41 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 179377.44 | 19275379.2 | 51.28 | 5510.4
22 | Khanpur | Bagho Bahar | Rural | 12853 | 199 | 59.7 | 767324.1 | 33 | 172.3 | 2657486.28 | 344.6 | 5314972.56 | 32 | 411296 | 89 | 1143917 | 232 | 0 | 80 | 12853 | 175 | 12853 | 16 | 12853 | 96 | 0 | 300 | 0 | 3836106.38 | 389835345.9 | 298.46 | 30330.3
23 | Khanpur | Nawan Kot | Rural | 4860 | 241 | 72.3 | 351378 | 15 | 183.7 | 1071338.4 | 367.4 | 2142676.8 | 36 | 174960 | 102 | 495720 | 256 | 0 | 80 | 4860 | 175 | 4860 | 16 | 4860 | 96 | 4860 | 300 | 0 | 1597676.4 | 159357942 | 328.74 | 32789.7
24 | Khanpur | Khanpur | Rural | 7985 | 170 | 51 | 407235 | 15 | 134 | 1283988 | 268 | 2567976 | 4 | 31940 | 20 | 159700 | 185 | 0 | 80 | 7985 | 175 | 7985 | 16 | 0 | 96 | 0 | 300 | 0 | 1723163 | 164882265 | 215.8 | 20649
25 | Khanpur | Dinpur Sharif | Rural | 4017 | 199 | 59.7 | 239814.9 | 21 | 160.3 | 772710.12 | 320.6 | 1545420.24 | 36 | 144612 | 90 | 361530 | 220 | 0 | 80 | 4017 | 175 | 4017 | 16 | 4017 | 96 | 0 | 300 | 0 | 1157137.02 | 115136459.1 | 288.06 | 28662.3
26 | Khanpur | Hamid Abad | Rural | 7966 | 291 | 87.3 | 695431.8 | 41 | 244.7 | 2339136.24 | 489.4 | 4678272.48 | 612 | 4875192 | 635 | 5058410 | 332 | 0 | 80 | 7966 | 175 | 7966 | 16 | 7966 | 96 | 7966 | 300 | 0 | 7909760.04 | 586287244.2 | 992.94 | 73598.7
27 | Khanpur | Haroon Abad | Rural | 6172 | 295 | 88.5 | 546222 | 30 | 236.5 | 1751613.6 | 473 | 3503227.2 | 900 | 5554800 | 995 | 6141140 | 325 | 0 | 80 | 6172 | 175 | 6172 | 16 | 6172 | 96 | 6172 | 300 | 0 | 7852635.6 | 580300698 | 1272.3 | 94021.5
28 | Khanpur | Pacca Laran | Rural | 5197 | 160 | 48 | 249456 | 25 | 137 | 854386.8 | 274 | 1708773.6 | 902 | 4687694 | 991 | 5150227 | 185 | 0 | 80 | 5197 | 175 | 5197 | 16 | 5197 | 96 | 5197 | 300 | 0 | 5791536.8 | 412288404 | 1114.4 | 79332
29 | Khanpur | M.A.Bachaya | Rural | 8917 | 210 | 63 | 561771 | 40 | 187 | 2000974.8 | 374 | 4001949.6 | 705 | 6286485 | 801 | 7142517 | 250 | 0 | 80 | 8917 | 175 | 8917 | 16 | 8917 | 96 | 8917 | 300 | 0 | 8849230.8 | 670353309 | 992.4 | 75177
30 | Khanpur | Kot Samaba | Rural | 11234 | 251 | 75.3 | 845920.2 | 54 | 229.7 | 3096539.76 | 459.4 | 6193079.52 | 35 | 393190 | 151 | 1696334 | 305 | 0 | 80 | 11234 | 175 | 11234 | 16 | 11234 | 96 | 11234 | 300 | 0 | 4335649.96 | 475902571.8 | 385.94 | 42362.7
31 | Khanpur | Waheed Shaheed | Rural | 5784 | 89 | 26.7 | 154432.8 | 37 | 99.3 | 689221.44 | 198.6 | 1378442.88 | 15 | 86760 | 45 | 260280 | 126 | 0 | 80 | 5784 | 175 | 5784 | 16 | 0 | 96 | 0 | 300 | 0 | 930414.24 | 98786671.2 | 160.86 | 17079.3
32 | Khanpur | Islam Garh | Rural | 9465 | 198 | 59.4 | 562221 | 18 | 156.6 | 1778662.8 | 313.2 | 3557325.6 | 405 | 3833325 | 425 | 4022625 | 216 | 0 | 80 | 9465 | 175 | 9465 | 16 | 9465 | 96 | 9465 | 300 | 0 | 6174208.8 | 456483699 | 652.32 | 48228.6
33 | Khanpur | Jangi | Rural | 5698 | 211 | 63.3 | 360683.4 | 21 | 168.7 | 1153503.12 | 337.4 | 2307006.24 | 518 | 2951564 | 550 | 3133900 | 232 | 0 | 80 | 5698 | 175 | 5698 | 16 | 5698 | 96 | 5698 | 300 | 0 | 4465750.52 | 327536424.6 | 783.74 | 57482.7
34 | Khanpur | Qazi Zaffar | Rural | 7264 | 211 | 63.3 | 459811.2 | 21 | 168.7 | 1470524.16 | 337.4 | 2941048.32 | 991 | 7198624 | 999 | 7256736 | 232 | 0 | 80 | 7264 | 175 | 7264 | 16 | 7264 | 96 | 7264 | 300 | 0 | 9128959.36 | 613246492.8 | 1256.74 | 84422.7
35 | Khanpur | G.Wala MWQ-02 | Rural | 5578 | 325 | 97.5 | 543855 | 10 | 237.5 | 1589730 | 475 | 3179460 | 800 | 4462400 | 841 | 4691098 | 335 | 0 | 80 | 5578 | 175 | 5578 | 16 | 5578 | 96 | 5578 | 300 | 0 | 6595985 | 473865045 | 1182.5 | 84952.5
36 | Khanpur | M.Nagar MWQ-03 | Rural | 5956 | 211 | 63.3 | 377014.8 | 25 | 172.7 | 1234321.44 | 345.4 | 2468642.88 | 551 | 3281756 | 591 | 3519996 | 236 | 0 | 80 | 5956 | 175 | 5956 | 16 | 5956 | 96 | 5956 | 300 | 0 | 4893092.24 | 360449377.2 | 821.54 | 60518.7
37 | Khanpur | Zahir Pir | Rural | 6391 | 311 | 93.3 | 596280.3 | 35 | 252.7 | 1938006.84 | 505.4 | 3876013.68 | 580 | 3706780 | 610 | 3898510 | 346 | 0 | 80 | 6391 | 175 | 6391 | 16 | 6391 | 96 | 6391 | 300 | 0 | 6241067.14 | 468260261.7 | 976.54 | 73268.7
38 | Khanpur | Abdul Sattar | Rural | 5565 | 280 | 84 | 467460 | 12 | 208 | 1389024 | 416 | 2778048 | 320 | 1780800 | 335 | 1864275 | 292 | 0 | 80 | 5565 | 175 | 5565 | 16 | 5565 | 96 | 5565 | 300 | 0 | 3637284 | 279941760 | 653.6 | 50304
39 | Khanpur | Jajjah Abbasian | Rural | 7819 | 180 | 54 | 422226 | 24 | 150 | 1407420 | 300 | 2814840 | 51 | 398769 | 99 | 774081 | 204 | 0 | 80 | 7819 | 175 | 7819 | 16 | 7819 | 96 | 7819 | 300 | 0 | 2228415 | 216601938 | 285 | 27702
40 | Khanpur | Chachran MWQ-10 | Rural | 11050 | 389 | 116.7 | 1289535 | 41 | 313.3 | 4154358 | 626.6 | 8308716 | 600 | 6630000 | 701 | 7746050 | 430 | 0 | 80 | 11050 | 175 | 11050 | 16 | 11050 | 96 | 11050 | 300 | 0 | 12073893 | 967154565 | 1092.66 | 87525.3
41 | Khanpur | FPK | Rural | 10064 | 398 | 119.4 | 1201641.6 | 41 | 319.6 | 3859745.28 | 639.2 | 7719490.56 | 15 | 150960 | 51 | 513264 | 439 | 0 | 80 | 10064 | 175 | 10064 | 16 | 0 | 96 | 0 | 300 | 0 | 5212346.88 | 497570198.4 | 517.92 | 49440.6
42 | Khanpur | City Zahir Pir | Rural | 8894 | 389 | 116.7 | 1037929.8 | 9 | 281.3 | 3002258.64 | 562.6 | 6004517.28 | 33 | 293502 | 105 | 933870 | 398 | 0 | 80 | 8894 | 175 | 8894 | 16 | 8894 | 96 | 8894 | 300 | 0 | 4333690.44 | 419417026.2 | 487.26 | 47157.3
43 | Khanpur | Chughati MWQ-04 | Rural | 4124 | 398 | 119.4 | 492405.6 | 45 | 323.6 | 1601431.68 | 647.2 | 3202863.36 | 475 | 1958900 | 501 | 2066124 | 443 | 0 | 80 | 4124 | 175 | 4124 | 16 | 4124 | 96 | 4124 | 300 | 0 | 4052737.28 | 317616458.4 | 982.72 | 77016.6
44 | Khanpur | Y.Abad MWQ-05 | Rural | 4104 | 351 | 105.3 | 432151.2 | 101 | 346.7 | 1707428.16 | 693.4 | 3414856.32 | 290 | 1190160 | 325 | 1333800 | 452 | 0 | 80 | 4104 | 175 | 4104 | 16 | 4104 | 96 | 4104 | 300 | 0 | 3329739.36 | 286215832.8 | 811.34 | 69740.7
45 | Khanpur | Sardar Garh MWQ-12 | Rural | 6219 | 230 | 69 | 429111 | 29 | 190 | 1417932 | 380 | 2835864 | 300 | 1865700 | 340 | 2114460 | 259 | 0 | 80 | 6219 | 175 | 6219 | 16 | 6219 | 96 | 6219 | 300 | 0 | 3712743 | 298306773 | 597 | 47967
46 | Khanpur | Lal Garh MWQ-01 | Rural | 4574 | 210 | 63 | 288162 | 24 | 171 | 938584.8 | 342 | 1877169.6 | 800 | 3659200 | 815 | 3727810 | 234 | 0 | 80 | 4574 | 175 | 4574 | 16 | 4574 | 96 | 4574 | 300 | 0 | 4885946.8 | 337163262 | 1068.2 | 73713
47 | Khanpur | N.Abad MWQ-6 | Rural | 4032 | 231 | 69.3 | 279417.6 | 41 | 202.7 | 980743.68 | 405.4 | 1961487.36 | 951 | 3834432 | 968 | 3902976 | 272 | 0 | 80 | 4032 | 175 | 4032 | 16 | 4032 | 96 | 4032 | 300 | 0 | 5094593.28 | 352706054.4 | 1263.54 | 87476.7
48 | Khanpur | Shahpur MWQ-8 | Rural | 3578 | 198 | 59.4 | 212533.2 | 8 | 146.6 | 629441.76 | 293.2 | 1258883.52 | 989 | 3538642 | 999 | 3574422 | 206 | 0 | 80 | 3578 | 175 | 3578 | 16 | 3578 | 96 | 3578 | 300 | 0 | 4380616.96 | 290635930.8 | 1224.32 | 81228.6
49 | Khanpur | MWQ-11 | Rural | 4968 | 180 | 54 | 268272 | 41 | 167 | 995587.2 | 334 | 1991174.4 | 789 | 3919752 | 898 | 4461264 | 221 | 0 | 80 | 4968 | 175 | 4968 | 16 | 4968 | 96 | 4968 | 300 | 0 | 5183611.2 | 387951120 | 1043.4 | 78090
50 | Khanpur | Thul Hassan | Rural | 3464 | 189 | 56.7 | 196408.8 | 15 | 147.3 | 612296.64 | 294.6 | 1224593.28 | 999 | 3460536 | 1012 | 3505568 | 204 | 0 | 80 | 3464 | 175 | 3464 | 16 | 3464 | 96 | 3464 | 300 | 0 | 4269241.44 | 284398903.2 | 1232.46 | 82101.3
51 | Khanpur | Abad Pur | Rural | 4038 | 189 | 56.7 | 228954.6 | 39 | 171.3 | 830051.28 | 342.6 | 1660102.56 | 989 | 3993582 | 1021 | 4122798 | 228 | 0 | 80 | 4038 | 175 | 4038 | 16 | 4038 | 96 | 4038 | 300 | 0 | 5052587.88 | 347660897.4 | 1251.26 | 86097.3
52 | Liaqat Pur | Saline Zone | Rural | 296 | 164 | 49.2 | 14563.2 | 51 | 165.8 | 58892.16 | 331.6 | 117784.32 | 1891 | 559736 | 2011 | 595256 | 215 | 0 | 80 | 296 | 175 | 296 | 16 | 296 | 96 | 296 | 300 | 0 | 633191.36 | 42826108.8 | 2139.16 | 144682.8
53 | Liaqat Pur | K.M.Khan | Rural | 5959 | 164 | 49.2 | 293182.8 | 125 | 239.8 | 1714761.84 | 479.6 | 3429523.68 | 12 | 71508 | 25 | 148975 | 289 | 0 | 80 | 5959 | 175 | 5959 | 16 | 0 | 96 | 0 | 300 | 0 | 2079452.64 | 215589469.2 | 348.96 | 36178.8
54 | Liaqat Pur | Allah Abad | Rural | 7665 | 164 | 49.2 | 377118 | 121 | 235.8 | 2168888.4 | 471.6 | 4337776.8 | 21 | 160965 | 43 | 329595 | 285 | 0 | 80 | 7665 | 175 | 7665 | 16 | 7665 | 96 | 0 | 300 | 0 | 2706971.4 | 281173662 | 353.16 | 36682.8
55 | Liaqat Pur | Rais Pathan | Rural | 4598 | 132 | 39.6 | 182080.8 | 124 | 216.4 | 1194008.64 | 432.8 | 2388017.28 | 18 | 82764 | 41 | 188518 | 256 | 0 | 80 | 4598 | 175 | 4598 | 16 | 4598 | 96 | 0 | 300 | 0 | 1458853.44 | 155138359.2 | 317.28 | 33740.4
56 | Liaqat Pur | Maitla | Rural | 8601 | 215 | 64.5 | 554764.5 | 123 | 273.5 | 2822848.2 | 547 | 5645696.4 | 401 | 3449001 | 415 | 3569415 | 338 | 0 | 80 | 8601 | 175 | 8601 | 16 | 8601 | 96 | 8601 | 300 | 0 | 6826613.7 | 554570977.5 | 793.7 | 64477.5
57 | Liaqat Pur | Tranda | Rural | 10405 | 132 | 39.6 | 412038 | 71 | 163.4 | 2040212.4 | 326.8 | 4080424.8 | 20 | 208100 | 45 | 468225 | 203 | 0 | 80 | 10405 | 175 | 10405 | 16 | 10405 | 96 | 0 | 300 | 0 | 2660350.4 | 274155102 | 255.68 | 26348.4
58 | Liaqat Pur | Abbasia | Rural | 6855 | 164 | 49.2 | 337266 | 65 | 179.8 | 1479034.8 | 359.6 | 2958069.6 | 20 | 137100 | 45 | 308475 | 229 | 0 | 80 | 6855 | 175 | 6855 | 16 | 6855 | 96 | 0 | 300 | 0 | 1953400.8 | 197004474 | 284.96 | 28738.8
59 | Liaqat Pur | City Feroza | Rural | 11486 | 265 | 79.5 | 913137 | 91 | 276.5 | 3811054.8 | 553 | 7622109.6 | 33 | 379038 | 71 | 815506 | 356 | 0 | 80 | 11486 | 175 | 11486 | 16 | 11486 | 96 | 0 | 300 | 0 | 5103229.8 | 508996347 | 444.3 | 44314.5
60 | Liaqat Pur | Rasheed Abad | Rural | 1525 | 165 | 49.5 | 75487.5 | 18 | 133.5 | 244305 | 267 | 488610 | 700 | 1067500 | 715 | 1090375 | 183 | 0 | 80 | 1525 | 175 | 1525 | 16 | 1525 | 96 | 1525 | 300 | 0 | 1387292.5 | 94965562.5 | 909.7 | 62272.5
61 | Liaqat Pur | Amin Abad | Rural | 5869 | 345 | 103.5 | 607441.5 | 61 | 302.5 | 2130447 | 605 | 4260894 | 251 | 1473119 | 265 | 1555285 | 406 | 0 | 80 | 5869 | 175 | 5869 | 16 | 5869 | 96 | 5869 | 300 | 0 | 4211007.5 | 350793064.5 | 717.5 | 59770.5
62 | Liaqat Pur | Scarp-3 | Rural | 192 | 98 | 29.4 | 5644.8 | 15 | 83.6 | 19261.44 | 167.2 | 38522.88 | 3030 | 581760 | 3045 | 584640 | 113 | 0 | 80 | 192 | 175 | 192 | 16 | 192 | 96 | 192 | 300 | 0 | 606666.24 | 37406707.2 | 3159.72 | 194826.6
63 | Liaqat Pur | Abbasia | Rural | 7051 | 289 | 86.7 | 611321.7 | 41 | 243.3 | 2058609.96 | 486.6 | 4117219.92 | 29 | 204479 | 60 | 423060 | 330 | 0 | 80 | 7051 | 175 | 7051 | 16 | 7051 | 96 | 0 | 300 | 0 | 2874410.66 | 274250760.3 | 407.66 | 38895.3
64 | Liaqat Pur | Head Fareed | Rural | 6102 | 345 | 103.5 | 631557 | 71 | 312.5 | 2288250 | 625 | 4576500 | 120 | 732240 | 248 | 1513296 | 416 | 0 | 80 | 6102 | 175 | 6102 | 16 | 6102 | 96 | 6102 | 300 | 0 | 3652047 | 367282431 | 598.5 | 60190.5
65 | Liaqat Pur | Thull Hamza | Rural | 8900 | 165 | 49.5 | 440550 | 39 | 154.5 | 1650060 | 309 | 3300120 | 18 | 160200 | 36 | 320400 | 204 | 0 | 80 | 8900 | 175 | 8900 | 16 | 8900 | 96 | 0 | 300 | 0 | 2250810 | 218552850 | 252.9 | 24556.5
66 | Liaqat Pur | City Jun pur | Rural | 9286 | 365 | 109.5 | 1016817 | 27 | 282.5 | 3147954 | 565 | 6295908 | 250 | 2321500 | 265 | 2460790 | 392 | 0 | 80 | 9286 | 175 | 9286 | 16 | 9286 | 96 | 9286 | 300 | 0 | 6486271 | 528452331 | 698.5 | 56908.5
67 | Liaqat Pur | Malkani | Rural | 6465 | 215 | 64.5 | 416992.5 | 39 | 189.5 | 1470141 | 379 | 2940282 | 700 | 4525500 | 715 | 4622475 | 242 | 12 | 80 | 6465 | 175 | 6465 | 16 | 6465 | 96 | 6465 | 300 | 0 | 6412633.5 | 455016397.5 | 991.9 | 70381.5
68 | Liaqat Pur | Shedani Sharif | Rural | 7172 | 265 | 79.5 | 570174 | 21 | 206.5 | 1777221.6 | 413 | 3554443.2 | 701 | 5027572 | 718 | 5149496 | 286 | 0 | 80 | 7172 | 175 | 7172 | 16 | 7172 | 96 | 7172 | 300 | 0 | 7374967.6 | 523946874 | 1028.3 | 73054.5
69 | Liaqat Pur | City Khan Bela | Rural | 6625 | 287 | 86.1 | 570412.5 | 36 | 236.9 | 1883355 | 473.8 | 3766710 | 18 | 119250 | 40 | 265000 | 323 | 0 | 80 | 6625 | 175 | 6625 | 16 | 6625 | 96 | 0 | 300 | 0 | 2573017.5 | 243613837.5 | 388.38 | 36771.9
70 | Liaqat Pur | Mud Ranjha | Rural | 4962 | 356 | 106.8 | 529941.6 | 33 | 282.2 | 1680331.68 | 564.4 | 3360663.36 | 412 | 2044344 | 430 | 2133660 | 389 | 0 | 80 | 4962 | 175 | 4962 | 16 | 4962 | 96 | 4962 | 300 | 0 | 4254617.28 | 331249226.4 | 857.44 | 66757.2
71 | Sadiqabad | Chaman | Rural | 5396 | 256 | 76.8 | 414412.8 | 33 | 212.2 | 1374037.44 | 424.4 | 2748074.88 | 99 | 534204 | 125 | 674500 | 289 | 0 | 80 | 5396 | 175 | 5396 | 16 | 5396 | 96 | 5396 | 300 | 0 | 2322654.24 | 206597731.2 | 430.44 | 38287.2
72 | Sadiqabad | NEW MANTHAR | Rural | 6971 | 156 | 46.8 | 326242.8 | 21 | 130.2 | 1089149.04 | 260.4 | 2178298.08 | 98 | 683158 | 145 | 1010795 | 177 | 0 | 80 | 6971 | 175 | 6971 | 16 | 6971 | 96 | 6971 | 300 | 0 | 2098549.84 | 192324313.2 | 301.04 | 27589.2
73 | Sadiqabad | Feeder NO-4 | Rural | 3358 | 145 | 43.5 | 146073 | 21 | 122.5 | 493626 | 245 | 987252 | 45 | 151110 | 54 | 181332 | 164 | 2 | 80 | 3358 | 175 | 3358 | 16 | 3358 | 96 | 0 | 300 | 0 | 790809 | 70553259 | 235.5 | 21010.5
74 | Sadiqabad | EXPRESS-1 | Rural | 4571 | 256 | 76.8 | 351052.8 | 24 | 203.2 | 1114592.64 | 406.4 | 2229185.28 | 657 | 3003147 | 685 | 3131135 | 280 | 0 | 80 | 4571 | 175 | 4571 | 16 | 4571 | 96 | 4571 | 300 | 0 | 4468792.44 | 322672375.2 | 977.64 | 70591.2
75 | Sadiqabad | EXPRESS-2 | Rural | 9511 | 265 | 79.5 | 756124.5 | 30 | 215.5 | 2459544.6 | 431 | 4919089.2 | 98 | 932078 | 125 | 1188875 | 295 | 0 | 80 | 9511 | 175 | 9511 | 16 | 9511 | 96 | 9511 | 300 | 0 | 4147747.1 | 368746225.5 | 436.1 | 38770.5
76 | Sadiqabad | Adam Sahaba | Rural | 3848 | 120 | 36 | 138528 | 27 | 111 | 512553.6 | 222 | 1025107.2 | 98 | 377104 | 125 | 481000 | 147 | 0 | 80 | 3848 | 175 | 3848 | 16 | 3848 | 96 | 3848 | 300 | 0 | 1028185.6 | 90782016 | 267.2 | 23592
77 | Sadiqabad | Tillu Bangla | Rural | 2293 | 89 | 26.7 | 61223.1 | 9 | 71.3 | 196189.08 | 142.6 | 392378.16 | 63 | 144459 | 75 | 171975 | 97 | 1 | 80 | 2293 | 175 | 0 | 16 | 2293 | 96 | 0 | 300 | 0 | 401871.18 | 34044858.9 | 175.26 | 14847.3
78 | Sadiqabad | RANG PUR (F.NO.5) | Rural | 5690 | 174 | 52.2 | 297018 | 21 | 142.8 | 975038.4 | 285.6 | 1950076.8 | 36 | 204840 | 75 | 426750 | 193 | 2 | 80 | 5690 | 175 | 5690 | 16 | 5690 | 96 | 0 | 300 | 0 | 1476896.4 | 143500662 | 259.56 | 25219.8
79 | Sadiqabad | SHAHBAZ PUR | Rural | 2447 | 178 | 53.4 | 130669.8 | 7 | 131.6 | 386430.24 | 263.2 | 772860.48 | 42 | 102774 | 120 | 293640 | 185 | 0 | 80 | 2447 | 175 | 2447 | 16 | 2447 | 96 | 2447 | 300 | 0 | 619874.04 | 64382038.2 | 253.32 | 26310.6
80 | Sadiqabad | PAKA MANA | Rural | 1275 | 165 | 49.5 | 63112.5 | 21 | 136.5 | 208845 | 273 | 417690 | 12 | 15300 | 25 | 31875 | 186 | 0 | 80 | 1275 | 175 | 1275 | 16 | 0 | 96 | 0 | 300 | 0 | 287257.5 | 27163237.5 | 225.3 | 21304.5
81 | Sadiqabad | BAHODI PUR | Rural | 2301 | 132 | 39.6 | 91119.6 | 24 | 116.4 | 321403.68 | 232.8 | 642807.36 | 33 | 75933 | 70 | 161070 | 155 | 1 | 80 | 2301 | 175 | 2301 | 16 | 2301 | 96 | 0 | 300 | 0 | 488456.28 | 48506000.4 | 212.28 | 21080.4
82 | Sadiqabad | KACHA MIANWALI | Rural | 702 | 198 | 59.4 | 41698.8 | 15 | 153.6 | 129392.64 | 307.2 | 258785.28 | 12 | 8424 | 30 | 21060 | 211 | 2 | 80 | 702 | 175 | 702 | 16 | 0 | 96 | 0 | 300 | 0 | 179515.44 | 16915813.2 | 255.72 | 24096.6
83 | Sadiqabad | KACHA RAZI | Rural | 1358 | 198 | 59.4 | 80665.2 | 15 | 153.6 | 250306.56 | 307.2 | 500613.12 | 8 | 10864 | 30 | 40740 | 212 | 1 | 80 | 1358 | 175 | 1358 | 16 | 0 | 96 | 0 | 300 | 0 | 341835.76 | 32723182.8 | 251.72 | 24096.6
84 | Sadiqabad | KACHA DINGRAHA | Rural | 605 | 196 | 58.8 | 35574 | 8 | 145.2 | 105415.2 | 290.4 | 210830.4 | 15 | 9075 | 45 | 27225 | 203 | 1 | 80 | 605 | 175 | 605 | 16 | 0 | 96 | 0 | 300 | 0 | 150064.2 | 14390046 | 248.04 | 23785.2
85 | Sadiqabad | CHAK DABA | Rural | 1266 | 140 | 42 | 53172 | 11 | 109 | 165592.8 | 218 | 331185.6 | 15 | 18990 | 45 | 56970 | 151 | 0 | 80 | 1266 | 175 | 1266 | 16 | 0 | 96 | 0 | 300 | 0 | 237754.8 | 23448852 | 187.8 | 18522
86 | Sadiqabad | RAJAN PUR KALAN | Rural | 4491 | 210 | 63 | 282933 | 14 | 161 | 867661.2 | 322 | 1735322.4 | 36 | 161676 | 73 | 327843 | 224 | 0 | 80 | 4491 | 175 | 4491 | 16 | 4491 | 96 | 0 | 300 | 0 | 1312270.2 | 124638723 | 292.2 | 27753
87 | Sadiqabad | SOAN MIANI (F.NO.9) | Rural | 1510 | 215 | 64.5 | 97395 | 15 | 165.5 | 299886 | 331 | 599772 | 16 | 24160 | 48 | 72480 | 230 | 0 | 80 | 1510 | 175 | 1510 | 16 | 0 | 96 | 0 | 300 | 0 | 421441 | 40627305 | 279.1 | 26905.5
88 | Sadiqabad | BADLI SHARIF | Rural | 4517 | 200 | 60 | 271020 | 24 | 164 | 888945.6 | 328 | 1777891.2 | 42 | 189714 | 87 | 392979 | 224 | 0 | 80 | 4517 | 175 | 4517 | 16 | 4517 | 96 | 0 | 300 | 0 | 1349679.6 | 131065272 | 298.8 | 29016
89 | Sadiqabad | Kot Karam Khan | Rural | 2728 | 240 | 72 | 196416 | 11 | 179 | 585974.4 | 358 | 1171948.8 | 39 | 106392 | 80 | 218240 | 238 | 13 | 80 | 2728 | 175 | 2728 | 16 | 2728 | 96 | 0 | 300 | 0 | 888782.4 | 84000576 | 325.8 | 30792
90 | Sadiqabad | BHONG | Rural | 2759 | 180 | 54 | 148986 | 21 | 147 | 486687.6 | 294 | 973375.2 | 21 | 57939 | 42 | 115878 | 199 | 2 | 80 | 2759 | 175 | 2759 | 16 | 2759 | 96 | 0 | 300 | 0 | 693612.6 | 65802150 | 251.4 | 23850
91 | Sadiqabad | SANJAR PUR(F.N.1) | Rural | 1617 | 80 | 24 | 38808 | 27 | 83 | 161053.2 | 166 | 322106.4 | 270 | 436590 | 178 | 287826 | 106 | 1 | 80 | 1617 | 175 | 1617 | 16 | 1617 | 96 | 1617 | 300 | 0 | 636451.2 | 36712368 | 393.6 | 22704
92 | Sadiqabad | Ahmed Pur Lamma | Rural | 5159 | 98 | 29.4 | 151674.6 | 12 | 80.6 | 498978.48 | 161.2 | 997956.96 | 120 | 619080 | 89 | 459151 | 109 | 1 | 80 | 5159 | 175 | 5159 | 16 | 5159 | 96 | 0 | 300 | 0 | 1269733.08 | 87881501.4 | 246.12 | 17034.6
93 | Sadiqabad | KHAWAJA FAREED | Rural | 5790 | 89 | 26.7 | 154593 | 33 | 95.3 | 662144.4 | 190.6 | 1324288.8 | 80 | 463200 | 45 | 260550 | 121 | 1 | 80 | 5790 | 175 | 5790 | 16 | 5790 | 96 | 0 | 300 | 0 | 1279937.4 | 95554107 | 221.06 | 16503.3
94 | Sadiqabad | KOT SABZAL | Rural | 3669 | 140 | 42 | 154098 | 42 | 140 | 616392 | 280 | 1232784 | 21 | 77049 | 78 | 286182 | 181 | 1 | 80 | 3669 | 175 | 3669 | 16 | 3669 | 96 | 0 | 300 | 0 | 847539 | 91600254 | 231 | 24966
95 | Sadiqabad | Walana | Rural | 2294 | 160 | 48 | 110112 | 9 | 121 | 333088.8 | 242 | 666177.6 | 59 | 135346 | 125 | 286750 | 169 | 0 | 80 | 2294 | 175 | 2294 | 16 | 2294 | 96 | 2294 | 300 | 0 | 578546.8 | 57505992 | 252.2 | 25068
96 | Sadiqabad | Musa Nawab | Rural | 6415 | 240 | 72 | 461880 | 15 | 183 | 1408734 | 366 | 2817468 | 102 | 654330 | 99 | 635085 | 255 | 0 | 80 | 6415 | 175 | 6415 | 16 | 6415 | 96 | 6415 | 300 | 0 | 2524944 | 208538820 | 393.6 | 32508
97 | Sadiqabad | Zaki Nagar | Rural | 3019 | 250 | 75 | 226425 | 15 | 190 | 688332 | 380 | 1376664 | 70 | 211330 | 102 | 307938 | 265 | 0 | 80 | 3019 | 175 | 3019 | 16 | 3019 | 96 | 3019 | 300 | 0 | 1126087 | 101755395 | 373 | 33705
98 | Sadiqabad | Walhar | Rural | 2480 | 120 | 36 | 89280 | 18 | 102 | 303552 | 204 | 607104 | 81 | 200880 | 105 | 260400 | 138 | 0 | 80 | 2480 | 175 | 2480 | 16 | 2480 | 96 | 2480 | 300 | 0 | 593712 | 52318080 | 239.4 | 21096
99 | Sadiqabad | Machi Goth | Rural | 5266 | 123 | 36.9 | 194315.4 | 12 | 98.1 | 619913.52 | 196.2 | 1239827.04 | 81 | 426546 | 90 | 473940 | 135 | 0 | 80 | 5266 | 175 | 5266 | 16 | 5266 | 96 | 0 | 300 | 0 | 1240774.92 | 103408968.6 | 235.62 | 19637.1
100 | Sadiqabad | Azad Nursery | Rural | 6162 | 298 | 89.4 | 550882.8 | 15 | 223.6 | 1653387.84 | 447.2 | 3306775.68 | 48 | 295776 | 201 | 1238562 | 313 | 0 | 80 | 6162 | 175 | 6162 | 16 | 6162 | 96 | 6162 | 300 | 0 | 2500046.64 | 274372909.2 | 405.72 | 44526.6
101 | Sadiqabad | MUSA NAGAR | Rural | 974 | 135 | 40.5 | 39447 | 30 | 124.5 | 145515.6 | 249 | 291031.2 | 180 | 175320 | 170 | 165580 | 163 | 2 | 80 | 974 | 175 | 974 | 16 | 974 | 96 | 974 | 300 | 0 | 360282.6 | 27515013 | 369.9 | 28249.5
102 | Sadiqabad | NAWAZ ABAD (F.NO.2) | Rural | 1833 | 60 | 18 | 32994 | 12 | 54 | 118778.4 | 108 | 237556.8 | 160 | 293280 | 151 | 276783 | 72 | 0 | 80 | 1833 | 175 | 0 | 16 | 1833 | 96 | 1833 | 300 | 0 | 445052.4 | 30959370 | 242.8 | 16890
103 | Sadiqabad | Kandir | Rural | 1400 | 80 | 24 | 33600 | 24 | 80 | 134400 | 160 | 268800 | 140 | 196000 | 130 | 182000 | 104 | 0 | 80 | 1400 | 175 | 1400 | 16 | 1400 | 96 | 1400 | 300 | 0 | 364000 | 27148800 | 260 | 19392
104 | Sadiqabad | MERAY SHAH | Rural | 2819 | 140 | 42 | 118398 | 39 | 137 | 463443.6 | 274 | 926887.2 | 120 | 338280 | 28 | 78932 | 179 | 0 | 80 | 2819 | 175 | 2819 | 16 | 2819 | 96 | 0 | 300 | 0 | 920121.6 | 60704346 | 326.4 | 21534
105 | Sadiqabad | MAHI | Rural | 2447 | 320 | 96 | 234912 | 54 | 278 | 816319.2 | 556 | 1632638.4 | 12 | 29364 | 42 | 102774 | 374 | 0 | 80 | 2447 | 175 | 2447 | 16 | 0 | 96 | 0 | 300 | 0 | 1080595.2 | 104829480 | 441.6 | 42840
106 | Sadiqabad | CHOWK CHADAR | Rural | 3194 | 389 | 116.7 | 372739.8 | 99 | 371.3 | 1423118.64 | 742.6 | 2846237.28 | 21 | 67074 | 45 | 143730 | 484 | 4 | 80 | 3194 | 175 | 3194 | 16 | 3194 | 96 | 0 | 300 | 0 | 1862932.44 | 180516256.2 | 583.26 | 56517.3
107 | Sadiqabad | JAFAR LAL | Rural | 2428 | 400 | 120 | 291360 | 63 | 343 | 999364.8 | 686 | 1998729.6 | 21 | 50988 | 40 | 97120 | 462 | 1 | 80 | 2428 | 175 | 2428 | 16 | 2428 | 96 | 0 | 300 | 0 | 1341712.8 | 126625056 | 552.6 | 52152
108 | Sadiqabad | GHAZI | Rural | 2576 | 190 | 57 | 146832 | 45 | 178 | 550233.6 | 356 | 1100467.2 | 18 | 46368 | 45 | 115920 | 234 | 1 | 80 | 2576 | 175 | 2576 | 16 | 2576 | 96 | 0 | 300 | 0 | 743433.6 | 73423728 | 288.6 | 28503
109 | Sadiqabad | RAHIM ABAD | Rural | 4107 | 398 | 119.4 | 490375.8 | 90 | 368.6 | 1816608.24 | 737.2 | 3633216.48 | 18 | 73926 | 50 | 205350 | 487 | 1 | 80 | 4107 | 175 | 4107 | 16 | 4107 | 96 | 0 | 300 | 0 | 2380910.04 | 231785116.2 | 579.72 | 56436.6
110 | Sadiqabad | Fazal Pur | Rural | 1219 | 145 | 43.5 | 53026.5 | 8 | 109.5 | 160176.6 | 219 | 320353.2 | 24 | 29256 | 15 | 18285 | 152 | 1 | 80 | 1219 | 175 | 1219 | 16 | 1219 | 96 | 0 | 300 | 0 | 242459.1 | 20477371.5 | 198.9 | 16798.5
111 | Sadiqabad | Abbasia | Rural | 1025 | 35 | 10.5 | 10762.5 | 05 | 29.5 | 36285 | 59 | 72570 | 05 | 5125 | 15 | 15375 | 39 | 1 | 80 | 0 | 175 | 0 | 16 | 1025 | 96 | 0 | 300 | 0 | 52172.5 | 5308987.5 | 50.9 | 5179.5
|  | TOTAL |  | 535011 | 18764 | 5629.2 | 32483095.8 | 3696 | 16408.8 | 114971391.84 | 32817.6 | 229942783.68 | 26516 | 121534886 | 29711 | 140588166 | 24510 | 52 | 80 | 519868 | 175 | 502872 | 16 | 413045 | 96 | 272816 | 300 | 0 | 268989373.64 | 22329306268.2 | 502.7735 | 41736.1629

## 400-220 (Rural) M-Garh
Statement of 400/220 V MEPCO Consumers For 2020-21
Muzaffargarh Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder | Category | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | M/Garh | KBS | Rural | 2955 | 580 | 174 | 514170 | 55 | 461 | 1634706 | 922 | 3269412 | 70 | 206850 | 135 | 398925 | 635 | 0 | 80 | 2955 | 175 | 2955 | 16 | 2955 | 96 | 2955 | 300 | 0 | 2355726 | 221642730 | 797.2 | 75006
2 | M/Garh | Muradabad | Rural | 3530 | 300 | 90 | 317700 | 30 | 240 | 1016640 | 480 | 2033280 | 40 | 141200 | 80 | 282400 | 330 | 0 | 80 | 3530 | 175 | 3530 | 16 | 3530 | 96 | 3530 | 300 | 0 | 1475540 | 139893900 | 418 | 39630
3 | M/Garh | T/Well # 03 | Rural | 8130 | 400 | 120 | 975600 | 33 | 313 | 3053628 | 626 | 6107256 | 72 | 585360 | 90 | 731700 | 433 | 0 | 80 | 8130 | 175 | 8130 | 16 | 8130 | 96 | 8130 | 300 | 0 | 4614588 | 413264160 | 567.6 | 50832
4 | M/Garh | Industrial Madina | Rural | 3355 | 250 | 75 | 251625 | 28 | 203 | 817278 | 406 | 1634556 | 50 | 167750 | 95 | 318725 | 278 | 0 | 80 | 3355 | 175 | 3355 | 16 | 3355 | 96 | 3355 | 300 | 0 | 1236653 | 117951735 | 368.6 | 35157
5 | M/Garh | Farid Colony | Rural | 7339 | 370 | 111 | 814629 | 40 | 299 | 2633233.2 | 598 | 5266466.4 | 85 | 623815 | 120 | 880680 | 410 | 0 | 80 | 7339 | 175 | 7339 | 16 | 7339 | 96 | 7339 | 300 | 0 | 4071677.2 | 371272671 | 554.8 | 50589
6 | M/Garh | Deenpur | Rural | 6610 | 320 | 96 | 634560 | 35 | 259 | 2054388 | 518 | 4108776 | 80 | 528800 | 120 | 793200 | 355 | 0 | 80 | 6610 | 175 | 6610 | 16 | 6610 | 96 | 6610 | 300 | 0 | 3217748 | 296022240 | 486.8 | 44784
7 | M/Garh | T/Well # 01 | Rural | 3826 | 460 | 138 | 527988 | 45 | 367 | 1684970.4 | 734 | 3369940.8 | 125 | 478250 | 150 | 573900 | 505 | 0 | 80 | 3826 | 175 | 3826 | 16 | 3826 | 96 | 3826 | 300 | 0 | 2691208.4 | 238214412 | 703.4 | 62262
8 | M/Garh | Wasanday Wali | Rural | 8898 | 905 | 271.5 | 2415807 | 60 | 693.5 | 7404915.6 | 1387 | 14809831.2 | 19 | 169062 | 58 | 516084 | 965 | 0 | 80 | 8898 | 175 | 8898 | 16 | 8898 | 96 | 8898 | 300 | 0 | 9989784.6 | 926802333 | 1122.7 | 104158.5
9 | M/Garh | Shahjamal | Rural | 13276 | 698 | 209.4 | 2779994.4 | 66 | 554.6 | 8835443.52 | 1109.2 | 17670887.04 | 158 | 2097608 | 161 | 2137436 | 764 | 0 | 80 | 13276 | 175 | 13276 | 16 | 13276 | 96 | 13276 | 300 | 0 | 13713045.92 | 1196839365.6 | 1032.92 | 90150.6
10 | M/Garh | Mondka | Rural | 9026 | 504 | 151.2 | 1364731.2 | 98 | 450.8 | 4882704.96 | 901.6 | 9765409.92 | 95 | 857470 | 217 | 1958642 | 602 | 0 | 80 | 9026 | 175 | 9026 | 16 | 9026 | 96 | 9026 | 300 | 0 | 7104906.16 | 707537308.8 | 787.16 | 78388.8
11 | M/Garh | Dani | Rural | 5865 | 1345 | 403.5 | 2366527.5 | 96 | 1037.5 | 7301925 | 2075 | 14603850 | 51 | 299115 | 102 | 598230 | 1441 | 0 | 80 | 5865 | 175 | 5865 | 16 | 5865 | 96 | 5865 | 300 | 5865 | 9967567.5 | 919224382.5 | 1699.5 | 156730.5
12 | M/Garh | Dewala | Rural | 2895 | 249 | 74.7 | 216256.5 | 65 | 239.3 | 831328.2 | 478.6 | 1662656.4 | 43 | 124485 | 59 | 170805 | 314 | 0 | 80 | 2895 | 175 | 2895 | 16 | 2895 | 96 | 2895 | 300 | 0 | 1172069.7 | 110656453.5 | 404.86 | 38223.3
13 | M/Garh | Miranpur | Rural | 3487 | 507 | 152.1 | 530372.7 | 60 | 414.9 | 1736107.56 | 829.8 | 3472215.12 | 17 | 59279 | 27 | 94149 | 567 | 0 | 80 | 3487 | 175 | 3487 | 16 | 3487 | 96 | 3487 | 300 | 0 | 2325759.26 | 215572965.3 | 666.98 | 61821.9
14 | M/Garh | Khangarh | Rural | 7900 | 290 | 87 | 687300 | 23 | 226 | 2142480 | 452 | 4284960 | 21 | 165900 | 43 | 339700 | 313 | 0 | 80 | 7900 | 175 | 7900 | 16 | 7900 | 96 | 7900 | 300 | 0 | 2995680 | 279541500 | 379.2 | 35385
15 | M/Garh | Kamalpur | Rural | 9479 | 531 | 159.3 | 1510004.7 | 96 | 467.7 | 5319993.96 | 935.4 | 10639987.92 | 93 | 881547 | 209 | 1981111 | 626 | 1 | 80 | 9479 | 175 | 9479 | 16 | 9479 | 96 | 9479 | 300 | 0 | 7711545.66 | 761795949.3 | 813.54 | 80366.7
16 | M/Garh | Shamsabad | Rural | 9345 | 824 | 247.2 | 2310084 | 127 | 703.8 | 7892413.2 | 1407.6 | 15784826.4 | 122 | 1140090 | 282 | 2635290 | 950 | 1 | 80 | 9345 | 175 | 9345 | 16 | 9345 | 96 | 9345 | 300 | 0 | 11342587.2 | 1112137236 | 1213.76 | 119008.8
17 | M/Garh | Khangarh-II | Rural | 3427 | 228 | 68.4 | 234406.8 | 89 | 248.6 | 1022342.64 | 497.2 | 2044685.28 | 54 | 185058 | 88 | 301576 | 317 | 0 | 80 | 3427 | 175 | 3427 | 16 | 3427 | 96 | 0 | 300 | 0 | 1441807.44 | 141478897.2 | 420.72 | 41283.6
18 | M/Garh | Sharif Ansari | Rural | 9044 | 401 | 120.3 | 1087993.2 | 18 | 298.7 | 3241731.36 | 597.4 | 6483462.72 | 45 | 406980 | 150 | 1356600 | 419 | 0 | 80 | 9044 | 175 | 9044 | 16 | 9044 | 96 | 9044 | 300 | 0 | 4736704.56 | 473667742.8 | 523.74 | 52373.7
19 | M/Garh | Ghazi Ghat | Rural | 5409 | 451 | 135.3 | 731837.7 | 19 | 334.7 | 2172470.76 | 669.4 | 4344941.52 | 49 | 265041 | 171 | 924939 | 470 | 0 | 80 | 5409 | 175 | 5409 | 16 | 5409 | 96 | 5409 | 300 | 0 | 3169349.46 | 318388344.3 | 585.94 | 58862.7
20 | M/Garh | Basira | Rural | 6699 | 456 | 136.8 | 916423.2 | 20 | 339.2 | 2726760.96 | 678.4 | 5453521.92 | 44 | 294756 | 96 | 643104 | 476 | 0 | 80 | 6699 | 175 | 6699 | 16 | 6699 | 96 | 6699 | 300 | 0 | 3937940.16 | 368546824.8 | 587.84 | 55015.2
21 | M/Garh | K.D. Qureshi | Rural | 13256 | 576 | 172.8 | 2290636.8 | 19 | 422.2 | 6716019.84 | 844.4 | 13432039.68 | 59 | 782104 | 174 | 2306544 | 595 | 0 | 80 | 13256 | 175 | 13256 | 16 | 13256 | 96 | 13256 | 300 | 0 | 9788760.64 | 951186931.2 | 738.44 | 71755.2
22 | M/Garh | Noor Kubra | Rural | 5636 | 342 | 102.6 | 578253.6 | 24 | 263.4 | 1781426.88 | 526.8 | 3562853.76 | 42 | 236712 | 93 | 524148 | 366 | 0 | 80 | 5636 | 175 | 5636 | 16 | 5636 | 96 | 5636 | 300 | 0 | 2596392.48 | 246954866.4 | 460.68 | 43817.4
23 | M/Garh | Mubariz Shaheed | Rural | 3550 | 96 | 28.8 | 102240 | 8 | 75.2 | 320352 | 150.4 | 640704 | 14 | 49700 | 23 | 81650 | 104 | 0 | 80 | 3550 | 175 | 3550 | 16 | 3550 | 96 | 3550 | 300 | 0 | 472292 | 43647960 | 133.04 | 12295.2
24 | M/Garh | Kunnal Sharif | Rural | 3778 | 236 | 70.8 | 267482.4 | 56 | 221.2 | 1002832.32 | 442.4 | 2005664.64 | 30 | 113340 | 67 | 253126 | 292 | 0 | 80 | 3778 | 175 | 3778 | 16 | 3778 | 96 | 3778 | 300 | 0 | 1383654.72 | 136329885.6 | 366.24 | 36085.2
25 | M/Garh | Darbar Manjhan Sultan | Rural | 3601 | 168 | 50.4 | 181490.4 | 45 | 162.6 | 702627.12 | 325.2 | 1405254.24 | 13 | 46813 | 27 | 97227 | 212 | 1 | 80 | 3601 | 175 | 3601 | 16 | 3601 | 96 | 3601 | 300 | 0 | 930930.52 | 90693345.6 | 258.52 | 25185.6
26 | M/Garh | Darbar Muhammad Musa | Rural | 4181 | 57 | 17.1 | 71495.1 | 31 | 70.9 | 355719.48 | 141.8 | 711438.96 | 7 | 29267 | 12 | 50172 | 88 | 0 | 80 | 4181 | 175 | 0 | 16 | 4181 | 96 | 4181 | 300 | 0 | 456481.58 | 45911142.9 | 109.18 | 10980.9
27 | M/Garh | Industrial Madina Express | Rural | 4509 | 236 | 70.8 | 319237.2 | 20 | 185.2 | 1002080.16 | 370.4 | 2004160.32 | 153 | 689877 | 33 | 148797 | 256 | 0 | 80 | 4509 | 175 | 4509 | 16 | 4509 | 96 | 4509 | 300 | 0 | 2011194.36 | 130135150.8 | 446.04 | 28861.2
28 | Kot Addu | Sinawan | Rural | 3569 | 132 | 39.6 | 141332.4 | 11 | 103.4 | 442841.52 | 206.8 | 885683.04 | 28 | 99932 | 76 | 271244 | 143 | 0 | 80 | 3569 | 175 | 3569 | 16 | 3569 | 96 | 0 | 300 | 0 | 684105.92 | 69839619.6 | 191.68 | 19568.4
29 | Kot Addu | T.P. Link +8+9 | Rural | 6115 | 318 | 95.4 | 583371 | 105 | 327.6 | 2403928.8 | 655.2 | 4807857.6 | 48 | 293520 | 89 | 544235 | 423 | 0 | 80 | 6115 | 175 | 6115 | 16 | 6115 | 96 | 0 | 300 | 0 | 3280819.8 | 322875669 | 536.52 | 52800.6
30 | Kot Addu | Feeder # 01 | Rural | 4969 | 152 | 45.6 | 226586.4 | 68 | 174.4 | 1039912.32 | 348.8 | 2079824.64 | 61 | 303109 | 129 | 641001 | 220 | 0 | 80 | 4969 | 175 | 4969 | 16 | 4969 | 96 | 4969 | 300 | 0 | 1569607.72 | 163929297.6 | 315.88 | 32990.4
31 | Kot Addu | Feeder # 02 | Rural | 9765 | 228 | 68.4 | 667926 | 89 | 248.6 | 2913094.8 | 497.2 | 5826189.6 | 54 | 527310 | 88 | 859320 | 317 | 0 | 80 | 9765 | 175 | 9765 | 16 | 9765 | 96 | 0 | 300 | 0 | 4108330.8 | 403134354 | 420.72 | 41283.6
32 | Kot Addu | Feeder # 07 | Rural | 4865 | 211 | 63.3 | 307954.5 | 126 | 273.7 | 1597860.6 | 547.4 | 3195721.2 | 38 | 184870 | 73 | 355145 | 337 | 0 | 80 | 4865 | 175 | 4865 | 16 | 4865 | 96 | 0 | 300 | 0 | 2090685.1 | 213975835.5 | 429.74 | 43982.7
33 | Kot Addu | Feeder # 03 | Rural | 7565 | 236 | 70.8 | 535602 | 143 | 308.2 | 2797839.6 | 616.4 | 5595679.2 | 89 | 673285 | 102 | 771630 | 379 | 0 | 80 | 7565 | 175 | 7565 | 16 | 7565 | 96 | 7565 | 300 | 0 | 4006726.6 | 383645358 | 529.64 | 50713.2
34 | Kot Addu | Feeder # 04 | Rural | 10799 | 303 | 90.9 | 981629.1 | 108 | 320.1 | 4148111.88 | 640.2 | 8296223.76 | 127 | 1371473 | 234 | 2526966 | 411 | 0 | 80 | 10799 | 175 | 10799 | 16 | 10799 | 96 | 10799 | 300 | 0 | 6501213.98 | 652336272.9 | 602.02 | 60407.1
35 | Kot Addu | Feeder # 5+6 | Rural | 9554 | 204 | 61.2 | 584704.8 | 86 | 228.8 | 2623146.24 | 457.6 | 5246292.48 | 78 | 745212 | 103 | 984062 | 290 | 0 | 80 | 9554 | 175 | 9554 | 16 | 9554 | 96 | 9554 | 300 | 0 | 3953063.04 | 375575383.2 | 413.76 | 39310.8
36 | Kot Addu | Feeder # 06 | Rural | 8590 | 176 | 52.8 | 453552 | 65 | 188.2 | 1939965.6 | 376.4 | 3879931.2 | 91 | 781690 | 208 | 1786720 | 241 | 0 | 80 | 8590 | 175 | 8590 | 16 | 8590 | 96 | 8590 | 300 | 0 | 3175207.6 | 341359728 | 369.64 | 39739.2
37 | Kot Addu | Feeder # 10 | Rural | 4083 | 237 | 71.1 | 290301.3 | 98 | 263.9 | 1293004.44 | 527.8 | 2586008.88 | 36 | 146988 | 76 | 310308 | 335 | 0 | 80 | 4083 | 175 | 4083 | 16 | 4083 | 96 | 0 | 300 | 0 | 1730293.74 | 174649916.7 | 423.78 | 42774.9
38 | Kot Addu | D.D.Panah-II | Rural | 8073 | 116 | 34.8 | 280940.4 | 40 | 121.2 | 1174137.12 | 242.4 | 2348274.24 | 65 | 524745 | 106 | 855738 | 156 | 0 | 80 | 8073 | 175 | 8073 | 16 | 8073 | 96 | 8073 | 300 | 0 | 1979822.52 | 193083555.6 | 245.24 | 23917.2
39 | Kot Addu | WAPDA Colony | Rural | 130 | 10 | 3 | 390 | 4 | 11 | 1716 | 22 | 3432 | 14 | 1820 | 41 | 5330 | 14 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 3926 | 526890 | 30.2 | 4053
40 | Kot Addu | City C.S.S | Rural | 10564 | 403 | 120.9 | 1277187.6 | 26 | 308.1 | 3905722.08 | 616.2 | 7811444.16 | 185 | 1954340 | 358 | 3781912 | 429 | 0 | 80 | 10564 | 175 | 10564 | 16 | 10564 | 96 | 10564 | 300 | 0 | 7137249.68 | 699432932.4 | 675.62 | 66209.1
41 | Kot Addu | Aziz Chowk | Rural | 8035 | 248 | 74.4 | 597804 | 27 | 200.6 | 1934185.2 | 401.2 | 3868370.4 | 156 | 1253460 | 230 | 1848050 | 275 | 0 | 80 | 8035 | 175 | 8035 | 16 | 8035 | 96 | 8035 | 300 | 0 | 3785449.2 | 344778636 | 471.12 | 42909.6
42 | Kot Addu | Bahar | Rural | 5873 | 554 | 166.2 | 976092.6 | 47 | 434.8 | 3064296.48 | 869.6 | 6128592.96 | 115 | 675395 | 168 | 986664 | 601 | 0 | 80 | 5873 | 175 | 5873 | 16 | 5873 | 96 | 5873 | 300 | 0 | 4715784.08 | 429843695.4 | 802.96 | 73189.8
43 | Kot Addu | Peer Jaggi Mor | Rural | 6775 | 461 | 138.3 | 936982.5 | 42 | 364.7 | 2965011 | 729.4 | 5930022 | 118 | 799450 | 174 | 1178850 | 503 | 0 | 80 | 6775 | 175 | 6775 | 16 | 6775 | 96 | 6775 | 300 | 0 | 4701443.5 | 429343267.5 | 693.94 | 63371.7
44 | Kot Addu | Riaz Abad | Rural | 8876 | 452 | 135.6 | 1203585.6 | 41 | 357.4 | 3806738.88 | 714.8 | 7613477.76 | 146 | 1295896 | 254 | 2254504 | 493 | 0 | 80 | 8876 | 175 | 8876 | 16 | 8876 | 96 | 8876 | 300 | 0 | 6306220.48 | 595689662.4 | 710.48 | 67112.4
45 | Kot Addu | Rangpur | Rural | 6614 | 1019 | 305.7 | 2021899.8 | 8 | 721.3 | 5724813.84 | 1442.6 | 11449627.68 | 17 | 112438 | 96 | 634944 | 1027 | 0 | 80 | 6614 | 175 | 6614 | 16 | 6614 | 96 | 6614 | 300 | 6614 | 7859151.64 | 731140000.2 | 1188.26 | 110544.3
46 | Kot Addu | Head Muhammad Wala | Rural | 1977 | 991 | 297.3 | 587762.1 | 16 | 709.7 | 1683692.28 | 1419.4 | 3367384.56 | 115 | 227355 | 213 | 421101 | 1007 | 0 | 80 | 1977 | 175 | 1977 | 16 | 1977 | 96 | 1977 | 300 | 0 | 2498809.38 | 229072419.9 | 1263.94 | 115868.7
47 | Kot Addu | City Gujrat | Rural | 8748 | 337 | 101.1 | 884422.8 | 18 | 253.9 | 2665340.64 | 507.8 | 5330681.28 | 116 | 1014768 | 326 | 2851848 | 355 | 0 | 80 | 8748 | 175 | 8748 | 16 | 8748 | 96 | 8748 | 300 | 0 | 4564531.44 | 493605025.2 | 521.78 | 56424.9
48 | Kot Addu | Mehmood Kot | Rural | 7297 | 489 | 146.7 | 1070469.9 | 22 | 364.3 | 3189956.52 | 728.6 | 6379913.04 | 54 | 394038 | 119 | 868343 | 511 | 0 | 80 | 7297 | 175 | 7297 | 16 | 7297 | 96 | 7297 | 300 | 0 | 4654464.42 | 438106772.1 | 637.86 | 60039.3
49 | Kot Addu | Gurmani | Rural | 9757 | 485 | 145.5 | 1419643.5 | 19 | 358.5 | 4197461.4 | 717 | 8394922.8 | 46 | 448822 | 101 | 985457 | 504 | 0 | 80 | 9757 | 175 | 9757 | 16 | 9757 | 96 | 9757 | 300 | 0 | 6065926.9 | 567081718.5 | 621.7 | 58120.5
50 | Kot Addu | Dibbi Shah | Rural | 6918 | 547 | 164.1 | 1135243.8 | 24 | 406.9 | 3377921.04 | 813.8 | 6755842.08 | 112 | 774816 | 253 | 1750254 | 571 | 0 | 80 | 6918 | 175 | 6918 | 16 | 6918 | 96 | 6918 | 300 | 0 | 5287980.84 | 513771496.2 | 764.38 | 74265.9
51 | Kot Addu | Al-Faisal | Rural | 6325 | 499 | 149.7 | 946852.5 | 33 | 382.3 | 2901657 | 764.6 | 5803314 | 49 | 309925 | 121 | 765325 | 532 | 0 | 80 | 6325 | 175 | 6325 | 16 | 6325 | 96 | 6325 | 300 | 0 | 4158434.5 | 396958897.5 | 657.46 | 62760.3
52 | Kot Addu | Madni | Rural | 9378 | 201 | 60.3 | 565493.4 | 18 | 158.7 | 1785946.32 | 317.4 | 3571892.64 | 98 | 919044 | 198 | 1856844 | 219 | 0 | 80 | 9378 | 175 | 9378 | 16 | 9378 | 96 | 9378 | 300 | 0 | 3270483.72 | 327420678.6 | 348.74 | 34913.7
53 | Kot Addu | Sultan Colony | Rural | 3159 | 331 | 99.3 | 313688.7 | 13 | 244.7 | 927608.76 | 489.4 | 1855217.52 | 20 | 63180 | 78 | 246402 | 342 | 2 | 80 | 3159 | 175 | 3159 | 16 | 3159 | 96 | 3159 | 300 | 0 | 1304477.46 | 127038237.3 | 412.94 | 40214.7
54 | Layyah | P/House-II | Rural | 8656 | 140 | 42 | 363552 | 47 | 145 | 1506144 | 290 | 3012288 | 77 | 666512 | 109 | 943504 | 187 | 0 | 80 | 8656 | 175 | 8656 | 16 | 8656 | 96 | 8656 | 300 | 0 | 2536208 | 238438176 | 293 | 27546
55 | Layyah | Mushtaq Abad | Rural | 3982 | 129 | 38.7 | 154103.4 | 26 | 116.3 | 555727.92 | 232.6 | 1111455.84 | 54 | 215028 | 88 | 350416 | 155 | 0 | 80 | 3982 | 175 | 3982 | 16 | 3982 | 96 | 3982 | 300 | 0 | 924859.32 | 88174620.6 | 232.26 | 22143.3
56 | Layyah | Karor | Rural | 5760 | 180 | 54 | 311040 | 32 | 158 | 1092096 | 316 | 2184192 | 55 | 316800 | 96 | 552960 | 212 | 0 | 80 | 5760 | 175 | 5760 | 16 | 5760 | 96 | 5760 | 300 | 0 | 1719936 | 165162240 | 298.6 | 28674
57 | Layyah | Kotla Haji Shah | Rural | 5180 | 84 | 25.2 | 130536 | 32 | 90.8 | 564412.8 | 181.6 | 1128825.6 | 88 | 455840 | 131 | 678580 | 116 | 0 | 80 | 5180 | 175 | 5180 | 16 | 5180 | 96 | 5180 | 300 | 0 | 1150788.8 | 108835944 | 222.16 | 21010.8
58 | Layyah | Fateh Sher | Rural | 3118 | 85 | 25.5 | 79509 | 26 | 85.5 | 319906.8 | 171 | 639813.6 | 56 | 174608 | 95 | 296210 | 111 | 0 | 80 | 3118 | 175 | 3118 | 16 | 3118 | 96 | 3118 | 300 | 0 | 574023.8 | 56399943 | 184.1 | 18088.5
59 | Layyah | Mian Bahadur | Rural | 7471 | 158 | 47.4 | 354125.4 | 50 | 160.6 | 1439811.12 | 321.2 | 2879622.24 | 39 | 291369 | 81 | 605151 | 208 | 0 | 80 | 7471 | 175 | 7471 | 16 | 7471 | 96 | 7471 | 300 | 0 | 2085305.52 | 210148770.6 | 279.12 | 28128.6
60 | Layyah | P/House-I | Rural | 4597 | 90 | 27 | 124119 | 24 | 87 | 479926.8 | 174 | 959853.6 | 60 | 275820 | 125 | 574625 | 114 | 0 | 80 | 4597 | 175 | 4597 | 16 | 4597 | 96 | 4597 | 300 | 0 | 879865.8 | 92441073 | 191.4 | 20109
61 | Layyah | Shah Habib | Rural | 4375 | 90 | 27 | 118125 | 22 | 85 | 446250 | 170 | 892500 | 51 | 223125 | 89 | 389375 | 112 | 0 | 80 | 4375 | 175 | 4375 | 16 | 4375 | 96 | 4375 | 300 | 0 | 787500 | 77266875 | 180 | 17661
62 | Layyah | Sh: Jalal ud Din | Rural | 5030 | 47 | 14.1 | 70923 | 12 | 44.9 | 271016.4 | 89.8 | 542032.8 | 48 | 241440 | 96 | 482880 | 59 | 0 | 80 | 0 | 175 | 0 | 16 | 5030 | 96 | 5030 | 300 | 0 | 583379.4 | 61707537 | 115.98 | 12267.9
63 | Layyah | Jamman Shah | Rural | 10532 | 568 | 170.4 | 1794652.8 | 25 | 422.6 | 5340987.84 | 845.2 | 10681975.68 | 53 | 558196 | 95 | 1000540 | 593 | 0 | 80 | 10532 | 175 | 10532 | 16 | 10532 | 96 | 10532 | 300 | 0 | 7693836.64 | 706334899.2 | 730.52 | 67065.6
64 | Layyah | Pir Jaggi | Rural | 9124 | 539 | 161.7 | 1475350.8 | 23 | 400.3 | 4382804.64 | 800.6 | 8765609.28 | 65 | 593060 | 178 | 1624072 | 562 | 0 | 80 | 9124 | 175 | 9124 | 16 | 9124 | 96 | 9124 | 300 | 0 | 6451215.44 | 627806929.2 | 707.06 | 68808.3
65 | Layyah | Indus | Rural | 6463 | 644 | 193.2 | 1248651.6 | 14 | 464.8 | 3604802.88 | 929.6 | 7209605.76 | 53 | 342539 | 79 | 510577 | 658 | 0 | 80 | 6463 | 175 | 6463 | 16 | 6463 | 96 | 6463 | 300 | 0 | 5195993.48 | 466956920.4 | 803.96 | 72250.8
66 | Layyah | Noori Hazoori | Rural | 7955 | 412 | 123.6 | 983238 | 14 | 302.4 | 2886710.4 | 604.8 | 5773420.8 | 75 | 596625 | 108 | 859140 | 426 | 0 | 80 | 7955 | 175 | 7955 | 16 | 7955 | 96 | 7955 | 300 | 0 | 4466573.4 | 400903362 | 561.48 | 50396.4
67 | Layyah | Samtia | Rural | 5866 | 429 | 128.7 | 754954.2 | 11 | 311.3 | 2191302.96 | 622.6 | 4382605.92 | 3 | 17598 | 11 | 64526 | 440 | 0 | 80 | 5866 | 175 | 5866 | 16 | 5866 | 96 | 5866 | 300 | 0 | 2963855.16 | 269092777.8 | 505.26 | 45873.3
68 | Layyah | Shahpur | Rural | 6721 | 369 | 110.7 | 744014.7 | 8 | 266.3 | 2147762.76 | 532.6 | 4295525.52 | 0 | 0 | 0 | 0 | 377 | 0 | 80 | 6721 | 175 | 6721 | 16 | 6721 | 96 | 6721 | 300 | 0 | 2891777.46 | 259963575.3 | 430.26 | 38679.3
69 | Layyah | Pir Swag | Rural | 5348 | 398 | 119.4 | 638551.2 | 13 | 291.6 | 1871372.16 | 583.2 | 3742744.32 | 3 | 16044 | 11 | 58828 | 411 | 0 | 80 | 5348 | 175 | 5348 | 16 | 5348 | 96 | 5348 | 300 | 0 | 2525967.36 | 230009992.8 | 472.32 | 43008.6
70 | Layyah | Waran Sehran | Rural | 8950 | 749 | 224.7 | 2011065 | 30 | 554.3 | 5953182 | 1108.6 | 11906364 | 3 | 26850 | 11 | 98450 | 779 | 0 | 80 | 8950 | 175 | 8950 | 16 | 8950 | 96 | 8950 | 300 | 0 | 7991097 | 726322035 | 892.86 | 81153.3
71 | Layyah | Talib Wala | Rural | 4636 | 381 | 114.3 | 529894.8 | 12 | 278.7 | 1550463.84 | 557.4 | 3100927.68 | 3 | 13908 | 11 | 50996 | 393 | 0 | 80 | 4636 | 175 | 4636 | 16 | 4636 | 96 | 4636 | 300 | 0 | 2094266.64 | 190705105.2 | 451.74 | 41135.7
72 | Layyah | Ali Rajan | Rural | 8505 | 410 | 123 | 1046115 | 14 | 301 | 3072006 | 602 | 6144012 | 7 | 59535 | 27 | 229635 | 424 | 0 | 80 | 8505 | 175 | 8505 | 16 | 8505 | 96 | 8505 | 300 | 0 | 4177656 | 385557165 | 491.2 | 45333
73 | Layyah | Maharan Canal | Rural | 3958 | 200 | 60 | 237480 | 30 | 170 | 807432 | 340 | 1614864 | 4 | 15832 | 14 | 55412 | 230 | 0 | 80 | 3958 | 175 | 3958 | 16 | 3958 | 96 | 3958 | 300 | 0 | 1060744 | 100929000 | 268 | 25500
74 | Layyah | Baroo Sharif | Rural | 3012 | 125 | 37.5 | 112950 | 10 | 97.5 | 352404 | 195 | 704808 | 2 | 6024 | 11 | 33132 | 135 | 0 | 80 | 3012 | 175 | 3012 | 16 | 3012 | 96 | 3012 | 300 | 0 | 471378 | 44615250 | 156.5 | 14812.5
75 | Layyah | Wakeel Wala | Rural | 6437 | 280 | 84 | 540708 | 50 | 246 | 1900202.4 | 492 | 3800404.8 | 2 | 12874 | 11 | 70807 | 330 | 0 | 80 | 6437 | 175 | 6437 | 16 | 6437 | 96 | 6437 | 300 | 0 | 2453784.4 | 233894832 | 381.2 | 36336
76 | Layyah | Head Tatar | Rural | 4203 | 220 | 66 | 277398 | 40 | 194 | 978458.4 | 388 | 1956916.8 | 4 | 16812 | 14 | 58842 | 260 | 0 | 80 | 4203 | 175 | 4203 | 16 | 4203 | 96 | 4203 | 300 | 0 | 1272668.4 | 121777722 | 302.8 | 28974
77 | Layyah | Asif Pully | Rural | 5358 | 180 | 54 | 289332 | 40 | 166 | 1067313.6 | 332 | 2134627.2 | 2 | 10716 | 11 | 58938 | 220 | 0 | 80 | 5358 | 175 | 5358 | 16 | 5358 | 96 | 5358 | 300 | 0 | 1367361.6 | 132481908 | 255.2 | 24726
78 | Layyah | Shaukat Wala | Rural | 5442 | 260 | 78 | 424476 | 40 | 222 | 1449748.8 | 444 | 2899497.6 | 2 | 10884 | 11 | 59862 | 300 | 0 | 80 | 5442 | 175 | 5442 | 16 | 5442 | 96 | 5442 | 300 | 0 | 1885108.8 | 178835004 | 346.4 | 32862
79 | Layyah | Shahi Dagar | Rural | 3270 | 160 | 48 | 156960 | 30 | 142 | 557208 | 284 | 1114416 | 4 | 13080 | 14 | 45780 | 190 | 0 | 80 | 3270 | 175 | 3270 | 16 | 3270 | 96 | 3270 | 300 | 0 | 727248 | 70082640 | 222.4 | 21432
80 | Layyah | Lalazar | Rural | 6204 | 399 | 119.7 | 742618.8 | 69 | 348.3 | 2593023.84 | 696.6 | 5186047.68 | 13 | 80652 | 27 | 167508 | 468 | 0 | 80 | 6204 | 175 | 6204 | 16 | 6204 | 96 | 6204 | 300 | 0 | 3416294.64 | 323441197.2 | 550.66 | 52134.3
81 | Layyah | Nawan Kot | Rural | 2700 | 545 | 163.5 | 441450 | 2 | 383.5 | 1242540 | 767 | 2485080 | 7 | 18900 | 24 | 64800 | 547 | 0 | 80 | 2700 | 175 | 2700 | 16 | 2700 | 96 | 2700 | 300 | 0 | 1702890 | 154317150 | 630.7 | 57154.5
82 | Layyah | Indus | Rural | 8598 | 160 | 48 | 412704 | 40 | 152 | 1568275.2 | 304 | 3136550.4 | 2 | 17196 | 11 | 94578 | 200 | 0 | 80 | 8598 | 175 | 8598 | 16 | 8598 | 96 | 8598 | 300 | 0 | 1998175.2 | 195105816 | 232.4 | 22692
83 | Layyah | Mauj Garh | Rural | 2077 | 130 | 39 | 81003 | 25 | 116 | 289118.4 | 232 | 578236.8 | 4 | 8308 | 14 | 29078 | 155 | 0 | 80 | 2077 | 175 | 2077 | 16 | 2077 | 96 | 2077 | 300 | 0 | 378429.4 | 36681897 | 182.2 | 17661
84 | Layyah | City (Choubara) | Rural | 1867 | 180 | 54 | 100818 | 7 | 133 | 297973.2 | 266 | 595946.4 | 15 | 28005 | 43 | 80281 | 187 | 0 | 80 | 1867 | 175 | 1867 | 16 | 1867 | 96 | 1867 | 300 | 0 | 426796.2 | 40876098 | 228.6 | 21894
85 | Layyah | Turko | Rural | 5355 | 577 | 173.1 | 926950.5 | 21 | 424.9 | 2730407.4 | 849.8 | 5460814.8 | 40 | 214200 | 69 | 369495 | 598 | 0 | 80 | 5355 | 175 | 5355 | 16 | 5355 | 96 | 5355 | 300 | 0 | 3871557.9 | 352599439.5 | 722.98 | 65844.9
86 | Layyah | Ladhana | Rural | 3761 | 166 | 49.8 | 187297.8 | 53 | 169.2 | 763633.44 | 338.4 | 1527266.88 | 18 | 67698 | 37 | 139157 | 219 | 0 | 80 | 3761 | 175 | 3761 | 16 | 3761 | 96 | 3761 | 300 | 0 | 1018629.24 | 100547326.2 | 270.84 | 26734.2
87 | Layyah | Dhori | Rural | 6158 | 398 | 119.4 | 735265.2 | 57 | 335.6 | 2479949.76 | 671.2 | 4959899.52 | 14 | 86212 | 31 | 190898 | 455 | 0 | 80 | 6158 | 175 | 6158 | 16 | 6158 | 96 | 6158 | 300 | 0 | 3301426.96 | 311253646.8 | 536.12 | 50544.6
88 | Layyah | Rafique Abad | Rural | 7490 | 335 | 100.5 | 752745 | 66 | 300.5 | 2700894 | 601 | 5401788 | 17 | 127330 | 38 | 284620 | 401 | 0 | 80 | 7490 | 175 | 7490 | 16 | 7490 | 96 | 7490 | 300 | 0 | 3580969 | 343442715 | 478.1 | 45853.5
89 | Layyah | Darbar Kamal Chishti | Rural | 3432 | 88 | 26.4 | 90604.8 | 40 | 101.6 | 418429.44 | 203.2 | 836858.88 | 6 | 20592 | 17 | 58344 | 128 | 0 | 80 | 3432 | 175 | 3432 | 16 | 3432 | 96 | 3432 | 300 | 0 | 529626.24 | 53983987.2 | 154.32 | 15729.6
90 | Alipur | Kallar Wali | Rural | 7425 | 948 | 284.4 | 2111670 | 54 | 717.6 | 6393816 | 1435.2 | 12787632 | 14 | 103950 | 35 | 259875 | 1002 | 0 | 80 | 7425 | 175 | 7425 | 16 | 7425 | 96 | 7425 | 300 | 0 | 8609436 | 789185430 | 1159.52 | 106287.6
91 | Alipur | Sher Sultan | Rural | 9514 | 554 | 166.2 | 1581226.8 | 18 | 405.8 | 4632937.44 | 811.6 | 9265874.88 | 14 | 133196 | 34 | 323476 | 572 | 0 | 80 | 9514 | 175 | 9514 | 16 | 9514 | 96 | 9514 | 300 | 0 | 6347360.24 | 580104733.2 | 667.16 | 60973.8
92 | Alipur | Kand Sharif | Rural | 4794 | 773 | 231.9 | 1111728.6 | 19 | 560.1 | 3222143.28 | 1120.2 | 6444286.56 | 9 | 43146 | 21 | 100674 | 792 | 0 | 80 | 4794 | 175 | 4794 | 16 | 4794 | 96 | 4794 | 300 | 0 | 4377017.88 | 396032819.4 | 913.02 | 82610.1
93 | Alipur | Bait Mazari | Rural | 6233 | 1192 | 357.6 | 2228920.8 | 43 | 877.4 | 6562601.04 | 1754.8 | 13125202.08 | 21 | 130893 | 59 | 367747 | 1235 | 0 | 80 | 6233 | 175 | 6233 | 16 | 6233 | 96 | 6233 | 300 | 6233 | 8922414.84 | 816263707.2 | 1431.48 | 130958.4
94 | Alipur | Bakaini | Rural | 5512 | 711 | 213.3 | 1175709.6 | 27 | 524.7 | 3470575.68 | 1049.4 | 6941151.36 | 3 | 16536 | 3 | 16536 | 738 | 0 | 80 | 5512 | 175 | 5512 | 16 | 5512 | 96 | 5512 | 300 | 0 | 4662821.28 | 420988370.4 | 845.94 | 76376.7
95 | Alipur | Kotla | Rural | 6184 | 492 | 147.6 | 912758.4 | 41 | 385.4 | 2859976.32 | 770.8 | 5719952.64 | 38 | 234992 | 54 | 333936 | 533 | 0 | 80 | 6184 | 175 | 6184 | 16 | 6184 | 96 | 6184 | 300 | 0 | 4007726.72 | 365971593.6 | 648.08 | 59180.4
96 | Alipur | Masso Shah | Rural | 3746 | 384 | 115.2 | 431539.2 | 18 | 286.8 | 1289223.36 | 573.6 | 2578446.72 | 35 | 131110 | 41 | 153586 | 402 | 0 | 80 | 3746 | 175 | 3746 | 16 | 3746 | 96 | 3746 | 300 | 0 | 1851872.56 | 165216580.8 | 494.36 | 44104.8
97 | Alipur | Bukhari | Rural | 5513 | 546 | 163.8 | 903029.4 | 10 | 392.2 | 2594638.32 | 784.4 | 5189276.64 | 8 | 44104 | 16 | 88208 | 556 | 0 | 80 | 5513 | 175 | 5513 | 16 | 5513 | 96 | 5513 | 300 | 0 | 3541771.72 | 319358166.6 | 642.44 | 57928.2
98 | Alipur | Faiz Pur | Rural | 3737 | 290 | 87 | 325119 | 23 | 226 | 1013474.4 | 452 | 2026948.8 | 21 | 78477 | 43 | 160691 | 313 | 0 | 80 | 3737 | 175 | 3737 | 16 | 3737 | 96 | 3737 | 300 | 0 | 1417070.4 | 132233745 | 379.2 | 35385
99 | Alipur | Permit | Rural | 6149 | 531 | 159.3 | 979535.7 | 96 | 467.7 | 3451064.76 | 935.4 | 6902129.52 | 93 | 571857 | 209 | 1285141 | 626 | 1 | 80 | 6149 | 175 | 6149 | 16 | 6149 | 96 | 6149 | 300 | 0 | 5002457.46 | 494174838.3 | 813.54 | 80366.7
100 | Alipur | Jhuggi Wala | Rural | 9016 | 824 | 247.2 | 2228755.2 | 127 | 703.8 | 7614552.96 | 1407.6 | 15229105.92 | 122 | 1099952 | 282 | 2542512 | 950 | 1 | 80 | 9016 | 175 | 9016 | 16 | 9016 | 96 | 9016 | 300 | 0 | 10943260.16 | 1072983340.8 | 1213.76 | 119008.8
101 | Alipur | Ram Pur | Rural | 5832 | 849 | 254.7 | 1485410.4 | 127 | 721.3 | 5047945.92 | 1442.6 | 10095891.84 | 115 | 670680 | 211 | 1230552 | 973 | 3 | 80 | 5832 | 175 | 5832 | 16 | 5832 | 96 | 5832 | 300 | 0 | 7204036.32 | 684042861.6 | 1235.26 | 117291.3
102 | Alipur | Hamzay Wala | Rural | 6179 | 371 | 111.3 | 687722.7 | 88 | 347.7 | 2578125.96 | 695.4 | 5156251.92 | 80 | 494320 | 171 | 1056609 | 457 | 2 | 80 | 6179 | 175 | 6179 | 16 | 6179 | 96 | 6179 | 300 | 0 | 3760168.66 | 374834823.3 | 608.54 | 60662.7
103 | Alipur | Beelay Wala | Rural | 5801 | 587 | 176.1 | 1021556.1 | 107 | 517.9 | 3605205.48 | 1035.8 | 7210410.96 | 100 | 580100 | 244 | 1415444 | 693 | 1 | 80 | 5801 | 175 | 5801 | 16 | 5801 | 96 | 5801 | 300 | 0 | 5206861.58 | 520615965.9 | 897.58 | 89745.9
104 | Alipur | Sithari | Rural | 4718 | 636 | 190.8 | 900194.4 | 108 | 553.2 | 3131997.12 | 1106.4 | 6263994.24 | 710 | 3349780 | 781 | 3684758 | 742 | 2 | 80 | 4718 | 175 | 4718 | 16 | 4718 | 96 | 4718 | 300 | 0 | 7381971.52 | 599625717.6 | 1564.64 | 127093.2
105 | Alipur | Khair Pur Sadat | Rural | 10889 | 1295 | 388.5 | 4230376.5 | 60 | 966.5 | 12629062.2 | 1933 | 25258124.4 | 9 | 98001 | 16 | 174224 | 1355 | 0 | 80 | 10889 | 175 | 10889 | 16 | 10889 | 96 | 10889 | 300 | 10889 | 16957439.7 | 1538632033.5 | 1557.3 | 141301.5
106 | Alipur | Bidani | Rural | 5068 | 896 | 268.8 | 1362278.4 | 53 | 680.2 | 4136704.32 | 1360.4 | 8273408.64 | 13 | 65884 | 27 | 136836 | 948 | 1 | 80 | 5068 | 175 | 5068 | 16 | 5068 | 96 | 5068 | 300 | 0 | 5564866.72 | 508701513.6 | 1098.04 | 100375.2
107 | Alipur | Seet Pur | Rural | 7517 | 678 | 203.4 | 1528957.8 | 54 | 528.6 | 4768183.44 | 1057.2 | 9536366.88 | 11 | 82687 | 14 | 105238 | 730 | 2 | 80 | 7517 | 175 | 7517 | 16 | 7517 | 96 | 7517 | 300 | 0 | 6379828.24 | 583083166.2 | 848.72 | 77568.6
108 | Alipur | Alloday Wali | Rural | 6712 | 1263 | 378.9 | 2543176.8 | 119 | 1003.1 | 8079368.64 | 2006.2 | 16158737.28 | 44 | 295328 | 119 | 798728 | 1379 | 3 | 80 | 6712 | 175 | 6712 | 16 | 6712 | 96 | 6712 | 300 | 6712 | 10917873.44 | 1025077447.2 | 1626.62 | 152723.1
109 | Alipur | Habib | Rural | 4616 | 649 | 194.7 | 898735.2 | 105 | 559.3 | 3098074.56 | 1118.6 | 6196149.12 | 35 | 161560 | 82 | 378512 | 750 | 4 | 80 | 4616 | 175 | 4616 | 16 | 4616 | 96 | 4616 | 300 | 0 | 4158369.76 | 397175872.8 | 900.86 | 86043.3
110 | Alipur | Mochi Wali | Rural | 9531 | 559 | 167.7 | 1598348.7 | 69 | 460.3 | 5264543.16 | 920.6 | 10529086.32 | 65 | 619515 | 180 | 1715580 | 623 | 5 | 80 | 9531 | 175 | 9531 | 16 | 9531 | 96 | 9531 | 300 | 0 | 7482406.86 | 739475025.3 | 785.06 | 77586.3
111 | Alipur | Banday Shah | Rural | 4707 | 129 | 38.7 | 182160.9 | 16 | 106.3 | 600424.92 | 212.6 | 1200849.84 | 66 | 310662 | 120 | 564840 | 139 | 6 | 80 | 4707 | 175 | 4707 | 16 | 4707 | 96 | 4707 | 300 | 0 | 1093247.82 | 106487873.1 | 232.26 | 22623.3
112 | Alipur | Mud Wala | Rural | 6837 | 254 | 76.2 | 520979.4 | 48 | 225.8 | 1852553.52 | 451.6 | 3705107.04 | 56 | 382872 | 79 | 540123 | 295 | 7 | 80 | 6837 | 175 | 6837 | 16 | 6837 | 96 | 6837 | 300 | 0 | 2756404.92 | 256276740.6 | 403.16 | 37483.8
113 | Alipur | Latti | Rural | 7244 | 273 | 81.9 | 593283.6 | 49 | 240.1 | 2087141.28 | 480.2 | 4174282.56 | 117 | 847548 | 140 | 1014160 | 314 | 8 | 80 | 7244 | 175 | 7244 | 16 | 7244 | 96 | 7244 | 300 | 0 | 3527972.88 | 313086404.4 | 487.02 | 43220.1
114 | Alipur | Latti-II | Rural | 3387 | 273 | 81.9 | 277395.3 | 24 | 215.1 | 874252.44 | 430.2 | 1748504.88 | 38 | 128706 | 75 | 254025 | 288 | 9 | 80 | 3387 | 175 | 3387 | 16 | 3387 | 96 | 3387 | 300 | 0 | 1280353.74 | 120983978.7 | 378.02 | 35720.1
115 | Alipur | Punjnad | Rural | 8149 | 406 | 121.8 | 992548.2 | 56 | 340.2 | 3326747.76 | 680.4 | 6653495.52 | 87 | 708963 | 111 | 904539 | 452 | 10 | 80 | 8149 | 175 | 8149 | 16 | 8149 | 96 | 8149 | 300 | 0 | 5028258.96 | 456459715.8 | 617.04 | 56014.2
116 | Alipur | Faqeer Shah | Rural | 2844 | 94 | 28.2 | 80200.8 | 26 | 91.8 | 313295.04 | 183.6 | 626590.08 | 43 | 122292 | 67 | 190548 | 109 | 11 | 80 | 2844 | 175 | 2844 | 16 | 2844 | 96 | 2844 | 300 | 0 | 515787.84 | 49268887.2 | 181.36 | 17323.8
117 | Alipur | Jinnah | Rural | 4916 | 44 | 13.2 | 64891.2 | 13 | 43.8 | 258384.96 | 87.6 | 516769.92 | 22 | 108152 | 7 | 34412 | 45 | 12 | 80 | 0 | 175 | 0 | 16 | 4916 | 96 | 4916 | 300 | 0 | 431428.16 | 33265588.8 | 87.76 | 6766.8
|  | TOTAL |  | 650212 | 2551 | 12722.4 | 85748799.9 | 1032 | 34309.6 | 276763468.92 | 68619.2 | 553526937.84 | 783 | 41144416 | 1413 | 75867023 | 53089 | 0 | 80 | 645052 | 175 | 640871 | 16 | 650082 | 96 | 618258 | 300 | 29601 | 403656684.82 | 38020884050.1 | 620.8078 | 58474.5961

## 400-220 (Rural) B-Nagar
Statement of 400/220 V MEPCO Consumers For 2020-21
Bahawal Nagar Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | B.W.N | SCARP FORDWAH | Rural | 8253 | 862 | 258.6 | 2134225.8 | 67 | 670.4 | 6639373.44 | 1340.8 | 13278746.88 | 99 | 817047 | 147 | 1213191 | 929 | 0 | 80 | 8253 | 175 | 8253 | 16 | 8253 | 96 | 8253 | 300 | 0 | 9590646.24 | 875918950.2 | 1162.08 | 106133.4
2 | B.W.N | SCARP DHUDDY | Rural | 4702 | 483 | 144.9 | 681319.8 | 49 | 387.1 | 2184173.04 | 774.2 | 4368346.08 | 79 | 371458 | 129 | 606558 | 532 | 0 | 80 | 4702 | 175 | 4702 | 16 | 4702 | 96 | 4702 | 300 | 0 | 3236950.84 | 300538204.2 | 688.42 | 63917.1
3 | B.W.N | IBRAHIM SHAHEED | Rural | 2471 | 469 | 140.7 | 347669.7 | 54 | 382.3 | 1133595.96 | 764.6 | 2267191.92 | 108 | 266868 | 173 | 427483 | 523 | 0 | 80 | 2471 | 175 | 2471 | 16 | 2471 | 96 | 2471 | 300 | 0 | 1748133.66 | 162723504.3 | 707.46 | 65853.3
4 | B.W.N | QABULA ROAD | Rural | 8311 | 574 | 172.2 | 1431154.2 | 56 | 457.8 | 4565730.96 | 915.6 | 9131461.92 | 193 | 1604023 | 338 | 2809118 | 630 | 0 | 80 | 8311 | 175 | 8311 | 16 | 8311 | 96 | 8311 | 300 | 0 | 7600908.16 | 720728257.8 | 914.56 | 86719.8
5 | B.W.N | RASHEED SHAHEED | Rural | 2404 | 141 | 42.3 | 101689.2 | 6 | 104.7 | 302038.56 | 209.4 | 604077.12 | 49 | 117796 | 55 | 132220 | 147 | 0 | 80 | 2404 | 175 | 2404 | 16 | 2404 | 96 | 0 | 300 | 0 | 521523.76 | 44482894.8 | 216.94 | 18503.7
6 | B.W.N | QAISER SHAHEED | Rural | 1835 | 120 | 36 | 66060 | 11 | 95 | 209190 | 190 | 418380 | 36 | 66060 | 45 | 82575 | 131 | 0 | 80 | 1835 | 175 | 1835 | 16 | 1835 | 96 | 0 | 300 | 0 | 341310 | 30255480 | 186 | 16488
7 | B.W.N | JALWALA | Rural | 9791 | 376 | 112.8 | 1104424.8 | 61 | 324.2 | 3809090.64 | 648.4 | 7618181.28 | 113 | 1106383 | 172 | 1684052 | 437 | 0 | 80 | 9791 | 175 | 9791 | 16 | 9791 | 96 | 9791 | 300 | 0 | 6019898.44 | 561447271.2 | 614.84 | 57343.2
8 | B.W.N | INDUSTRIAL | Rural | 6519 | 413 | 123.9 | 807704.1 | 19 | 308.1 | 2410204.68 | 616.2 | 4820409.36 | 55 | 358545 | 91 | 593229 | 432 | 0 | 80 | 6519 | 175 | 6519 | 16 | 6519 | 96 | 0 | 300 | 0 | 3576453.78 | 327241413.9 | 548.62 | 50198.1
9 | B.W.N | MAHAR WALI | Rural | 7248 | 433 | 129.9 | 941515.2 | 44 | 347.1 | 3018936.96 | 694.2 | 6037873.92 | 704 | 5102592 | 830 | 6015840 | 477 | 0 | 80 | 7248 | 175 | 7248 | 16 | 7248 | 96 | 7248 | 300 | 0 | 9063044.16 | 726047380.8 | 1250.42 | 100172.1
10 | B.W.N | ADDA KHARAJ PURA | Rural | 6744 | 185 | 55.5 | 374292 | 16 | 145.5 | 1177502.4 | 291 | 2355004.8 | 165 | 1112760 | 199 | 1342056 | 201 | 0 | 80 | 6744 | 175 | 6744 | 16 | 6744 | 96 | 6744 | 300 | 0 | 2664554.4 | 222946524 | 395.1 | 33058.5
11 | B.W.N | PAK PATTAN ROAD | Rural | 4828 | 367 | 110.1 | 531562.8 | 13 | 269.9 | 1563692.64 | 539.8 | 3127385.28 | 33 | 159324 | 91 | 439348 | 380 | 0 | 80 | 4828 | 175 | 4828 | 16 | 4828 | 96 | 0 | 300 | 0 | 2254579.44 | 215598685.2 | 466.98 | 44655.9
12 | B.W.N | MEHMOOD | Rural | 3856 | 690 | 207 | 798192 | 39 | 522 | 2415398.4 | 1044 | 4830796.8 | 23 | 88688 | 76 | 293056 | 729 | 0 | 80 | 3856 | 175 | 3856 | 16 | 3856 | 96 | 0 | 300 | 0 | 3302278.4 | 309825744 | 856.4 | 80349
13 | B.W.N | FIDAI SHAH | Rural | 6332 | 855 | 256.5 | 1624158 | 42 | 640.5 | 4866775.2 | 1281 | 9733550.4 | 29 | 183628 | 95 | 601540 | 897 | 0 | 80 | 6332 | 175 | 6332 | 16 | 6332 | 96 | 0 | 300 | 0 | 6674561.2 | 624977898 | 1054.1 | 98701.5
14 | B.W.N | MCD-II | Rural | 2853 | 204 | 61.2 | 174603.6 | 18 | 160.8 | 550514.88 | 321.6 | 1101029.76 | 16 | 45648 | 54 | 154062 | 222 | 0 | 80 | 2853 | 175 | 2853 | 16 | 0 | 96 | 0 | 300 | 0 | 770766.48 | 75829316.4 | 270.16 | 26578.8
15 | B.W.N | ANWAR SAHEED | Rural | 1791 | 293 | 87.9 | 157428.9 | 27 | 232.1 | 498829.32 | 464.2 | 997658.64 | 22 | 39402 | 79 | 141489 | 320 | 0 | 80 | 1791 | 175 | 1791 | 16 | 1791 | 96 | 0 | 300 | 0 | 695660.22 | 68821145.1 | 388.42 | 38426.1
16 | B.W.N | M.S.GUNJ ROAD | Rural | 2026 | 93 | 27.9 | 56525.4 | 10 | 75.1 | 182583.12 | 150.2 | 365166.24 | 7 | 14182 | 26 | 52676 | 103 | 0 | 80 | 2026 | 175 | 2026 | 16 | 0 | 96 | 0 | 300 | 0 | 253290.52 | 25240110.6 | 125.02 | 12458.1
17 | B.W.N | TAKHAT MAHAL | Rural | 6117 | 534 | 160.2 | 979943.4 | 43 | 416.8 | 3059478.72 | 833.6 | 6118957.44 | 61 | 373137 | 86 | 526062 | 577 | 0 | 80 | 6117 | 175 | 6117 | 16 | 6117 | 96 | 0 | 300 | 0 | 4412559.12 | 401640996.6 | 721.36 | 65659.8
18 | B.W.N | JUND WALA | Rural | 6213 | 137 | 41.1 | 255354.3 | 36 | 131.9 | 983393.64 | 263.8 | 1966787.28 | 61 | 378993 | 97 | 602661 | 173 | 0 | 80 | 6213 | 175 | 6213 | 16 | 6213 | 96 | 6213 | 300 | 0 | 1617740.94 | 154932959.7 | 260.38 | 24936.9
19 | B.W.N | FAQIR SHAH | Rural | 4895 | 169 | 50.7 | 248176.5 | 36 | 154.3 | 906358.2 | 308.6 | 1812716.4 | 174 | 851730 | 212 | 1037740 | 205 | 0 | 80 | 4895 | 175 | 4895 | 16 | 4895 | 96 | 4895 | 300 | 0 | 2006264.7 | 171771913.5 | 409.86 | 35091.3
20 | B.W.N | ABDULLAH | Rural | 5795 | 241 | 72.3 | 418978.5 | 29 | 197.7 | 1374805.8 | 395.4 | 2749611.6 | 68 | 394060 | 104 | 602680 | 270 | 0 | 80 | 5795 | 175 | 5795 | 16 | 5795 | 96 | 5795 | 300 | 0 | 2187844.3 | 202394431.5 | 377.54 | 34925.7
21 | B.W.N | MUQEEM SHAH | Rural | 4250 | 567 | 170.1 | 722925 | 48 | 444.9 | 2268990 | 889.8 | 4537980 | 65 | 276250 | 102 | 433500 | 615 | 0 | 80 | 4250 | 175 | 4250 | 16 | 4250 | 96 | 4250 | 300 | 0 | 3268165 | 300457575 | 768.98 | 70695.9
22 | H.Abad | AMRUKA | Rural | 8437 | 834 | 250.2 | 2110937.4 | 31 | 614.8 | 6224481.12 | 1229.6 | 12448962.24 | 25 | 210925 | 131 | 1105247 | 865 | 0 | 80 | 8437 | 175 | 8437 | 16 | 8437 | 96 | 8437 | 300 | 0 | 8546343.52 | 819585366.6 | 1012.96 | 97141.8
23 | H.Abad | DUNGA BUNGA | Rural | 5773 | 330 | 99 | 571527 | 46 | 277 | 1918945.2 | 554 | 3837890.4 | 161 | 929453 | 236 | 1362428 | 376 | 0 | 80 | 5773 | 175 | 5773 | 16 | 5773 | 96 | 5773 | 300 | 0 | 3419925.2 | 313733685 | 592.4 | 54345
24 | H.Abad | KHATAN | Rural | 6142 | 389 | 116.7 | 716771.4 | 36 | 308.3 | 2272294.32 | 616.6 | 4544588.64 | 139 | 853738 | 196 | 1203832 | 425 | 0 | 80 | 6142 | 175 | 6142 | 16 | 6142 | 96 | 6142 | 300 | 0 | 3842803.72 | 347055552.6 | 625.66 | 56505.3
25 | H.Abad | CITY DUNGA BUNGA | Rural | 5846 | 280 | 84 | 491064 | 43 | 239 | 1676632.8 | 478 | 3353265.6 | 136 | 795056 | 183 | 1069818 | 323 | 0 | 80 | 5846 | 175 | 5846 | 16 | 5846 | 96 | 5846 | 300 | 0 | 2962752.8 | 266858208 | 506.8 | 45648
26 | H.Abad | GHULAB ALI | Rural | 4291 | 337 | 101.1 | 433820.1 | 29 | 264.9 | 1364023.08 | 529.8 | 2728046.16 | 146 | 626486 | 194 | 832454 | 366 | 0 | 80 | 4291 | 175 | 4291 | 16 | 4291 | 96 | 4291 | 300 | 0 | 2424329.18 | 214931469.9 | 564.98 | 50088.9
27 | H.Abad | PULL MURAD | Rural | 9039 | 373 | 111.9 | 1011464.1 | 40 | 301.1 | 3265971.48 | 602.2 | 6531942.96 | 110 | 994290 | 169 | 1527591 | 413 | 0 | 80 | 9039 | 175 | 9039 | 16 | 9039 | 96 | 9039 | 300 | 0 | 5271725.58 | 486606429.9 | 583.22 | 53834.1
28 | H.Abad | MIAN WALA BUNGALOW | Rural | 9550 | 356 | 106.8 | 1019940 | 49 | 298.2 | 3417372 | 596.4 | 6834744 | 93 | 888150 | 155 | 1480250 | 405 | 0 | 80 | 9550 | 175 | 9550 | 16 | 9550 | 96 | 9550 | 300 | 0 | 5325462 | 501959460 | 557.64 | 52561.2
29 | H.Abad | DHARAN WALA ROAD | Rural | 6922 | 254 | 76.2 | 527456.4 | 29 | 206.8 | 1717763.52 | 413.6 | 3435527.04 | 105 | 726810 | 171 | 1183662 | 283 | 0 | 80 | 6922 | 175 | 6922 | 16 | 6922 | 96 | 6922 | 300 | 0 | 2972029.92 | 278733711.6 | 429.36 | 40267.8
30 | H.Abad | MUBARAK ABAD | Rural | 5312 | 246 | 73.8 | 392025.6 | 31 | 203.2 | 1295278.08 | 406.4 | 2590556.16 | 112 | 594944 | 187 | 993344 | 277 | 0 | 80 | 5312 | 175 | 5312 | 16 | 5312 | 96 | 5312 | 300 | 0 | 2282247.68 | 216210086.4 | 429.64 | 40702.2
31 | H.Abad | CITY FAQIR WALI | Rural | 7223 | 98 | 29.4 | 212356.2 | 4 | 72.6 | 629267.76 | 145.2 | 1258535.52 | 23 | 166129 | 75 | 541725 | 102 | 0 | 80 | 7223 | 175 | 0 | 16 | 7223 | 96 | 0 | 300 | 0 | 1007752.96 | 108652699.8 | 139.52 | 15042.6
32 | H.Abad | YATEEM WALA | Rural | 2723 | 70 | 21 | 57183 | 6 | 55 | 179718 | 110 | 359436 | 41 | 111643 | 116 | 315868 | 76 | 0 | 80 | 2723 | 175 | 0 | 16 | 2723 | 96 | 2723 | 300 | 0 | 348544 | 40689789 | 128 | 14943
33 | H.Abad | WAINS | Rural | 4699 | 84 | 25.2 | 118414.8 | 5 | 63.8 | 359755.44 | 127.6 | 719510.88 | 41 | 192659 | 99 | 465201 | 89 | 0 | 80 | 4699 | 175 | 0 | 16 | 4699 | 96 | 4699 | 300 | 0 | 670829.24 | 71437957.2 | 142.76 | 15202.8
34 | H.Abad | RURAL | Rural | 7424 | 127 | 38.1 | 282854.4 | 11 | 99.9 | 889989.12 | 199.8 | 1779978.24 | 43 | 319232 | 68 | 504832 | 138 | 0 | 80 | 7424 | 175 | 7424 | 16 | 7424 | 96 | 0 | 300 | 0 | 1492075.52 | 137937177.6 | 200.98 | 18579.9
35 | H.Abad | MEHRIA CITY | Rural | 8425 | 198 | 59.4 | 500445 | 13 | 151.6 | 1532676 | 303.2 | 3065352 | 26 | 219050 | 81 | 682425 | 211 | 0 | 80 | 8425 | 175 | 8425 | 16 | 8425 | 96 | 0 | 300 | 0 | 2252171 | 226367955 | 267.32 | 26868.6
36 | H.Abad | CANAL 7/R | Rural | 1122 | 52 | 15.6 | 17503.2 | 4 | 40.4 | 54394.56 | 80.8 | 108789.12 | 39 | 43758 | 95 | 106590 | 56 | 0 | 80 | 0 | 175 | 0 | 16 | 1122 | 96 | 0 | 300 | 0 | 115655.76 | 12975256.8 | 103.08 | 11564.4
37 | H.Abad | CITY-II FAQIR WALI | Rural | 4009 | 93 | 27.9 | 111851.1 | 0 | 65.1 | 313183.08 | 130.2 | 626366.16 | 22 | 88198 | 77 | 308693 | 93 | 0 | 80 | 4009 | 175 | 0 | 16 | 4009 | 96 | 0 | 300 | 0 | 513232.18 | 56439102.9 | 128.02 | 14078.1
38 | H.Abad | 75-ADDA | Rural | 1740 | 68 | 20.4 | 35496 | 2 | 49.6 | 103564.8 | 99.2 | 207129.6 | 40 | 69600 | 117 | 203580 | 70 | 0 | 80 | 0 | 175 | 0 | 16 | 1740 | 96 | 1740 | 300 | 0 | 208660.8 | 24749064 | 119.92 | 14223.6
39 | H.Abad | LATIF ABAD | Rural | 6502 | 150 | 45 | 292590 | 7 | 112 | 873868.8 | 224 | 1747737.6 | 39 | 253578 | 108 | 702216 | 157 | 0 | 80 | 6502 | 175 | 6502 | 16 | 6502 | 96 | 6502 | 300 | 0 | 1420036.8 | 147874986 | 218.4 | 22743
40 | H.Abad | QURAISH | Rural | 3779 | 161 | 48.3 | 182525.7 | 18 | 130.7 | 592698.36 | 261.4 | 1185396.72 | 25 | 94475 | 150 | 566850 | 179 | 0 | 80 | 3779 | 175 | 3779 | 16 | 3779 | 96 | 3779 | 300 | 0 | 869699.06 | 105682380.3 | 230.14 | 27965.7
41 | H.Abad | KHICHI WALA | Rural | 2628 | 36 | 10.8 | 28382.4 | 2 | 27.2 | 85777.92 | 54.4 | 171555.84 | 3 | 7884 | 126 | 331128 | 38 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 2628 | 300 | 0 | 122044.32 | 30246177.6 | 46.44 | 11509.2
42 | H.Abad | WALHAR | Rural | 7270 | 128 | 38.4 | 279168 | 12 | 101.6 | 886358.4 | 203.2 | 1772716.8 | 10 | 72700 | 130 | 945100 | 140 | 0 | 80 | 7270 | 175 | 7270 | 16 | 0 | 96 | 7270 | 300 | 0 | 1238226.4 | 163906512 | 170.32 | 22545.6
43 | H.Abad | RAFIQUE ABAD | Rural | 3324 | 29 | 8.7 | 28918.8 | 6 | 26.3 | 104905.44 | 52.6 | 209810.88 | 5 | 16620 | 129 | 428796 | 35 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 3324 | 300 | 0 | 150444.24 | 38403169.2 | 45.26 | 11553.3
44 | H.Abad | RAFIQUE SHAHEED | Rural | 3062 | 3 | 0.9 | 2755.8 | 2 | 4.1 | 15065.04 | 8.2 | 30130.08 | 2 | 6124 | 14 | 42868 | 5 | 0 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 23944.84 | 4388152.2 | 7.82 | 1433.1
45 | H.Abad | FAZAL SHAH | Rural | 3062 | 196 | 58.8 | 180045.6 | 12 | 149.2 | 548220.48 | 298.4 | 1096440.96 | 21 | 64302 | 103 | 315386 | 208 | 0 | 80 | 3062 | 175 | 3062 | 16 | 3062 | 96 | 3062 | 300 | 0 | 792568.08 | 85249754.4 | 258.84 | 27841.2
46 | H.Abad | GHAFOOR SHAHEED | Rural | 3513 | 202 | 60.6 | 212887.8 | 20 | 161.4 | 680397.84 | 322.8 | 1360795.68 | 41 | 144033 | 114 | 400482 | 222 | 0 | 80 | 3513 | 175 | 3513 | 16 | 3513 | 96 | 3513 | 300 | 0 | 1037318.64 | 106315324.2 | 295.28 | 30263.4
47 | H.Abad | CITY KHICHIWALA | Rural | 916 | 123 | 36.9 | 33800.4 | 12 | 98.1 | 107831.52 | 196.2 | 215663.04 | 17 | 15572 | 65 | 59540 | 135 | 0 | 80 | 916 | 175 | 916 | 16 | 916 | 96 | 0 | 300 | 0 | 157203.92 | 16613583.6 | 171.62 | 18137.1
48 | H.Abad | MARROT 1ST | Rural | 7448 |  | 0 | 0 | 286 | 286 | 2556153.6 | 572 | 5112307.2 | 56 | 417088 | 25.65 | 191041.2 | 286 | 0 | 80 | 7448 | 175 | 7448 | 16 | 7448 | 96 | 0 | 300 | 0 | 2973241.6 | 318200904 | 399.2 | 42723
49 | H.Abad | MANSOORA | Rural | 5260 |  | 0 | 0 | 291 | 291 | 1836792 | 582 | 3673584 | 52 | 273520 | 26 | 136760 | 291 | 0 | 80 | 5260 | 175 | 5260 | 16 | 5260 | 96 | 0 | 300 | 0 | 2110312 | 228620640 | 401.2 | 43464
50 | H.Abad | CHOLISTAN | Rural | 2742 |  | 0 | 0 | 111 | 111 | 365234.4 | 222 | 730468.8 | 44 | 120648 | 19.4 | 53194.8 | 111 | 0 | 80 | 2742 | 175 | 2742 | 16 | 2742 | 96 | 0 | 300 | 0 | 485882.4 | 47019816 | 177.2 | 17148
51 | H.Abad | ZIA | Rural | 1394 |  | 0 | 0 | 386 | 386 | 645700.8 | 772 | 1291401.6 | 66 | 92004 | 19.35 | 26973.9 | 386 | 0 | 80 | 1394 | 175 | 1394 | 16 | 1394 | 96 | 0 | 300 | 0 | 737704.8 | 79102530 | 529.2 | 56745
52 | Chishtian | ROHI | Rural | 3994 |  | 0 | 0 | 219 | 219 | 1049623.2 | 438 | 2099246.4 | 49 | 195706 | 23.6 | 94258.4 | 219 | 0 | 80 | 3994 | 175 | 3994 | 16 | 3994 | 96 | 0 | 300 | 0 | 1245329.2 | 131610288 | 311.8 | 32952
53 | Chishtian | SARDAR | Rural | 1362 |  | 0 | 0 | 145 | 145 | 236988 | 290 | 473976 | 49 | 66738 | 26.95 | 36705.9 | 145 | 0 | 80 | 1362 | 175 | 1362 | 16 | 1362 | 96 | 0 | 300 | 0 | 303726 | 30640914 | 223 | 22497
54 | Chishtian | CHAPPU | Rural | 1082 |  | 0 | 0 | 41 | 41 | 53234.4 | 82 | 106468.8 | 33 | 35706 | 26.95 | 29159.9 | 41 | 0 | 80 | 0 | 175 | 0 | 16 | 1082 | 96 | 0 | 300 | 0 | 88940.4 | 8137722 | 82.2 | 7521
55 | Chishtian | MEER GARH | Rural | 1436 |  | 0 | 0 | 269 | 269 | 463540.8 | 538 | 927081.6 | 64 | 91904 | 22.6 | 32453.6 | 269 | 0 | 80 | 1436 | 175 | 1436 | 16 | 1436 | 96 | 0 | 300 | 0 | 555444.8 | 57572112 | 386.8 | 40092
56 | Chishtian | MOHAR SHARIF | Rural | 6324 | 471 | 141.3 | 893581.2 | 21 | 350.7 | 2661392.16 | 701.4 | 5322784.32 | 32 | 202368 | 66 | 417384 | 492 | 0 | 80 | 6324 | 175 | 6324 | 16 | 6324 | 96 | 0 | 300 | 0 | 3757341.36 | 347090842.8 | 594.14 | 54884.7
57 | Chishtian | SHOUQ ELLAHI | Rural | 5250 | 438 | 131.4 | 689850 | 12 | 318.6 | 2007180 | 637.2 | 4014360 | 31 | 162750 | 66 | 346500 | 450 | 0 | 80 | 5250 | 175 | 5250 | 16 | 5250 | 96 | 0 | 300 | 0 | 2859780 | 263721150 | 544.72 | 50232.6
58 | Chishtian | MANGHAIR SHARIF | Rural | 5006 | 399 | 119.7 | 599218.2 | 10 | 289.3 | 1737882.96 | 578.6 | 3475765.92 | 57 | 285342 | 160 | 800960 | 409 | 0 | 80 | 5006 | 175 | 5006 | 16 | 5006 | 96 | 5006 | 300 | 0 | 2622443.16 | 258401209.8 | 523.86 | 51618.3
59 | Chishtian | GUJJIANI | Rural | 8915 | 288 | 86.4 | 770256 | 8 | 209.6 | 2242300.8 | 419.2 | 4484601.6 | 29 | 258535 | 48 | 427920 | 296 | 0 | 80 | 8915 | 175 | 8915 | 16 | 8915 | 96 | 0 | 300 | 0 | 3271091.8 | 297062064 | 366.92 | 33321.6
60 | Chishtian | SHEHR FARID | Rural | 3544 | 392 | 117.6 | 416774.4 | 18 | 292.4 | 1243518.72 | 584.8 | 2487037.44 | 85 | 301240 | 110 | 389840 | 410 | 0 | 80 | 3544 | 175 | 3544 | 16 | 3544 | 96 | 3544 | 300 | 0 | 1961533.12 | 173862969.6 | 553.48 | 49058.4
61 | Chishtian | AZEEM WAH | Rural | 5263 | 351 | 105.3 | 554193.9 | 24 | 269.7 | 1703317.32 | 539.4 | 3406634.64 | 115 | 605245 | 278 | 1463114 | 375 | 0 | 80 | 5263 | 175 | 5263 | 16 | 5263 | 96 | 5263 | 300 | 0 | 2862756.22 | 293847500.1 | 543.94 | 55832.7
62 | Chishtian | SAYEEDAN WALA | Rural | 2294 | 22 | 6.6 | 15140.4 | 1 | 16.4 | 45145.92 | 32.8 | 90291.84 | 19 | 43586 | 31 | 71114 | 23 | 0 | 80 | 0 | 175 | 0 | 16 | 2294 | 96 | 0 | 300 | 0 | 103872.32 | 9729771.6 | 45.28 | 4241.4
63 | Chishtian | SHEED CHOWK | Rural | 8190 | 195 | 58.5 | 479115 | 23 | 159.5 | 1567566 | 319 | 3135132 | 82 | 671580 | 137 | 1122030 | 218 | 0 | 80 | 8190 | 175 | 8190 | 16 | 8190 | 96 | 8190 | 300 | 0 | 2718261 | 256867065 | 331.9 | 31363.5
64 | Chishtian | AL-MURAD | Rural | 8359 | 160 | 48 | 401232 | 21 | 133 | 1334096.4 | 266 | 2668192.8 | 92 | 769028 | 136 | 1136824 | 181 | 0 | 80 | 8359 | 175 | 8359 | 16 | 8359 | 96 | 8359 | 300 | 0 | 2504356.4 | 229504704 | 299.6 | 27456
65 | Chishtian | AL-FATEH | Rural | 2906 | 73 | 21.9 | 63641.4 | 14 | 65.1 | 227016.72 | 130.2 | 454033.44 | 49 | 142394 | 70 | 203420 | 87 | 0 | 80 | 2906 | 175 | 0 | 16 | 2906 | 96 | 0 | 300 | 0 | 433052.12 | 39638130.6 | 149.02 | 13640.1
66 | Chishtian | CHOONA WALA | Rural | 5487 | 178 | 53.4 | 293005.8 | 12 | 136.6 | 899429.04 | 273.2 | 1798858.08 | 41 | 224967 | 55 | 301785 | 190 | 0 | 80 | 5487 | 175 | 5487 | 16 | 5487 | 96 | 0 | 300 | 0 | 1417401.84 | 126917602.2 | 258.32 | 23130.6
67 | Chishtian | BAKHSHAN KHAN | Rural | 4960 | 142 | 42.6 | 211296 | 13 | 112.4 | 669004.8 | 224.8 | 1338009.6 | 38 | 188480 | 66 | 327360 | 155 | 0 | 80 | 4960 | 175 | 4960 | 16 | 4960 | 96 | 0 | 300 | 0 | 1068780.8 | 100556064 | 215.48 | 20273.4
68 | Chishtian | AL-GHAZI | Rural | 4124 | 136 | 40.8 | 168259.2 | 17 | 112.2 | 555255.36 | 224.4 | 1110510.72 | 49 | 202076 | 61 | 251564 | 153 | 0 | 80 | 4124 | 175 | 4124 | 16 | 4124 | 96 | 0 | 300 | 0 | 925590.56 | 82229260.8 | 224.44 | 19939.2
69 | Chishtian | CITY CHOONA WALA | Rural | 5536 | 128 | 38.4 | 212582.4 | 5 | 94.6 | 628446.72 | 189.2 | 1256893.44 | 47 | 260192 | 60 | 332160 | 133 | 0 | 80 | 5536 | 175 | 5536 | 16 | 5536 | 96 | 0 | 300 | 0 | 1101221.12 | 95980953.6 | 198.92 | 17337.6
70 | Chishtian | NEW CHOLISTAN | Rural | 3005 | 107 | 32.1 | 96460.5 | 3 | 77.9 | 280907.4 | 155.8 | 561814.8 | 42 | 126210 | 63 | 189315 | 110 | 0 | 80 | 3005 | 175 | 3005 | 16 | 3005 | 96 | 0 | 300 | 0 | 503577.9 | 45357169.5 | 167.58 | 15093.9
|  | TOTAL |  | 343848 | 16903 | 5070.9 | 29674693.8 | 3144 | 14976.1 | 100240818.24 | 29952.2 | 200481636.48 | 4846 | 27971290 | 8087.5 | 45852879.7 | 20047 | 0 | 80 | 328596 | 175 | 307036 | 16 | 322685 | 96 | 199587 | 300 | 0 | 157886802.04 | 14869095052.2 | 459.1762 | 43243.221

## 400-220 (Rural) Khanewal
Statement of 400/220 V MEPCO Consumers For 2020-21
Khanewal Circle
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H=C2X0.9 | I=C2-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Name of Division | Name of Feeder |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | Khanewal | 17-AH | Rural | 4997 | 267 | 80.1 | 400259.7 | 23 | 209.9 | 1258644.36 | 419.8 | 2517288.72 | 5 | 24985 | 24.3 | 121427.1 | 290 | 0 | 80 | 4997 | 175 | 4997 | 16 | 0 | 96 | 0 | 300 | 0 | 1683889.06 | 159523728.3 | 336.98 | 31923.9
2 | Khanewal | Mahr Shah | Rural | 7290 | 202 | 60.6 | 441774 | 25 | 166.4 | 1455667.2 | 332.8 | 2911334.4 | 191 | 1392390 | 217.3 | 1584117 | 227 | 0 | 80 | 7290 | 175 | 7290 | 16 | 7290 | 96 | 7290 | 300 | 0 | 3289831.2 | 271052406 | 451.28 | 37181.4
3 | Khanewal | Industrial Estate | Rural | 1040 | 109 | 32.7 | 34008 | 18 | 94.3 | 117686.4 | 188.6 | 235372.8 | 489 | 508560 | 510.15 | 530556 | 127 | 0 | 80 | 1040 | 175 | 1040 | 16 | 1040 | 96 | 1040 | 300 | 0 | 660254.4 | 46057752 | 634.86 | 44286.3
4 | Khanewal | Kot Mela Ram | Rural | 6646 | 235 | 70.5 | 468543 | 29 | 193.5 | 1543201.2 | 387 | 3086402.4 | 11 | 73106 | 35.45 | 235600.7 | 264 | 0 | 80 | 6646 | 175 | 6646 | 16 | 0 | 96 | 0 | 300 | 0 | 2084850.2 | 200725815 | 313.7 | 30202.5
5 | Khanewal | Nanak Pur | Rural | 7273 | 177 | 53.1 | 386196.3 | 23 | 146.9 | 1282084.44 | 293.8 | 2564168.88 | 7 | 50911 | 29.4 | 213826.2 | 200 | 0 | 80 | 7273 | 175 | 7273 | 16 | 0 | 96 | 0 | 300 | 0 | 1719191.74 | 167838293.7 | 236.38 | 23076.9
6 | Khanewal | Kot Abbas Shaheed | Rural | 6488 | 288 | 86.4 | 560563.2 | 20 | 221.6 | 1725288.96 | 443.2 | 3450577.92 | 190 | 1232720 | 212.58 | 1379219.04 | 308 | 0 | 80 | 6488 | 175 | 6488 | 16 | 6488 | 96 | 6488 | 300 | 0 | 3518572.16 | 291469507.2 | 542.32 | 44924.4
7 | Khanewal | MARYALA | Rural | 4312 | 188 | 56.4 | 243196.8 | 24 | 155.6 | 805136.64 | 311.2 | 1610273.28 | 9 | 38808 | 33.25 | 143374 | 212 | 0 | 80 | 4312 | 175 | 4312 | 16 | 0 | 96 | 0 | 300 | 0 | 1087141.44 | 105948427.2 | 252.12 | 24570.6
8 | Khanewal | Vehniwal | Rural | 6891 | 316 | 94.8 | 653266.8 | 34 | 255.2 | 2110299.84 | 510.4 | 4220599.68 | 12 | 82692 | 67.1 | 462386.1 | 350 | 0 | 80 | 6891 | 175 | 6891 | 16 | 0 | 96 | 0 | 300 | 0 | 2846258.64 | 282938947.2 | 413.04 | 41059.2
9 | Khanewal | Kasrawan | Rural | 3671 | 238 | 71.4 | 262109.4 | 28 | 194.6 | 857251.92 | 389.2 | 1714503.84 | 7 | 25697 | 33.15 | 121693.65 | 265 | 1 | 80 | 3671 | 175 | 3671 | 16 | 0 | 96 | 0 | 300 | 0 | 1145058.32 | 110958177.6 | 311.92 | 30225.6
10 | Khanewal | Shanti Nager | Rural | 6608 | 216 | 64.8 | 428198.4 | 26 | 177.2 | 1405125.12 | 354.4 | 2810250.24 | 7 | 46256 | 28.2 | 186345.6 | 242 | 0 | 80 | 6608 | 175 | 6608 | 16 | 0 | 96 | 0 | 300 | 0 | 1879579.52 | 181080345.6 | 284.44 | 27403.2
11 | Khanewal | Jahangir Abad | Rural | 6518 | 56 | 16.8 | 109502.4 | 12 | 51.2 | 400465.92 | 102.4 | 800931.84 | 191 | 1244938 | 215.35 | 1403651.3 | 68 | 0 | 80 | 0 | 175 | 0 | 16 | 6518 | 96 | 6518 | 300 | 0 | 1754906.32 | 132603495.6 | 269.24 | 20344.2
12 | Khanewal | Pir Asghar Ali Shh | Rural | 4766 | 238 | 71.4 | 340292.4 | 37 | 203.6 | 1164429.12 | 407.2 | 2328858.24 | 6 | 28596 | 30 | 142980 | 275 | 0 | 80 | 4766 | 175 | 4766 | 16 | 0 | 96 | 0 | 300 | 0 | 1533317.52 | 149331171.6 | 321.72 | 31332.6
13 | Khanewal | Perowal-II | Rural | 5038 | 375 | 112.5 | 566775 | 31 | 293.5 | 1774383.6 | 587 | 3548767.2 | 133 | 670054 | 109 | 549142 | 406 | 0 | 80 | 5038 | 175 | 5038 | 16 | 5038 | 96 | 5038 | 300 | 0 | 3011212.6 | 247574877 | 597.7 | 49141.5
14 | Khanewal | Shaikh Malka | Rural | 3278 | 210 | 63 | 206514 | 29 | 176 | 692313.6 | 352 | 1384627.2 | 850 | 2786300 | 875 | 2868250 | 239 | 0 | 80 | 3278 | 175 | 3278 | 16 | 3278 | 96 | 3278 | 300 | 0 | 3685127.6 | 255792174 | 1124.2 | 78033
15 | Khanewal | Nawan Chowk | Rural | 5537 | 204 | 61.2 | 338864.4 | 21 | 163.8 | 1088352.72 | 327.6 | 2176705.44 | 5 | 27685 | 25.15 | 139255.55 | 225 | 0 | 80 | 5537 | 175 | 5537 | 16 | 0 | 96 | 0 | 300 | 0 | 1454902.12 | 139974252.6 | 262.76 | 25279.8
16 | Khanewal | Zahoor Abad | Rural | 4311 | 170 | 51 | 219861 | 22 | 141 | 729421.2 | 282 | 1458842.4 | 7 | 30177 | 34.15 | 147220.65 | 192 | 0 | 80 | 4311 | 175 | 4311 | 16 | 0 | 96 | 0 | 300 | 0 | 979459.2 | 97023366 | 227.2 | 22506
17 | Khanewal | 42/10-R | Rural | 2025 | 197 | 59.1 | 119677.5 | 17 | 154.9 | 376407 | 309.8 | 752814 | 28 | 56700 | 1.4292 | 2894.0625 | 214 | 0 | 80 | 2025 | 175 | 2025 | 16 | 2025 | 96 | 0 | 300 | 0 | 552784.5 | 45701516.25 | 272.98 | 22568.65
18 | Khanewal | City-II (JHN) | Rural | 9759 | 437 | 131.1 | 1279404.9 | 25 | 330.9 | 3875103.72 | 661.8 | 7750207.44 | 89 | 868551 | 6.9313 | 67642.0688 | 462 | 0 | 80 | 9759 | 175 | 9759 | 16 | 9759 | 96 | 0 | 300 | 0 | 6023059.62 | 472909185.225 | 617.18 | 48458.775
19 | Khanewal | City-III (JHN) | Rural | 2231 | 415 | 124.5 | 277759.5 | 26 | 316.5 | 847333.8 | 633 | 1694667.6 | 382 | 852242 | 19.8542 | 44294.6458 | 441 | 0 | 80 | 2231 | 175 | 2231 | 16 | 2231 | 96 | 0 | 300 | 0 | 1977335.3 | 105171013.25 | 886.3 | 47140.75
20 | Khanewal | Rahim Shah | Rural | 10129 | 285 | 85.5 | 866029.5 | 13 | 212.5 | 2582895 | 425 | 5165790 | 189 | 1914381 | 12.2014 | 123587.8681 | 298 | 0 | 80 | 10129 | 175 | 10129 | 16 | 10129 | 96 | 0 | 300 | 0 | 5363305.5 | 319960760.5833 | 529.5 | 31588.5833
21 | Khanewal | Industrial JHN | Rural | 3804 | 202 | 60.6 | 230522.4 | 11 | 152.4 | 695675.52 | 304.8 | 1391351.04 | 89 | 338556 | 4.6701 | 17765.2083 | 213 | 0 | 80 | 3804 | 175 | 3804 | 16 | 3804 | 96 | 0 | 300 | 0 | 1264753.92 | 85238542.1 | 332.48 | 22407.6083
22 | Khanewal | Multani Wala | Rural | 9104 | 527 | 158.1 | 1439342.4 | 36 | 404.9 | 4423451.52 | 809.8 | 8846903.04 | 63 | 573552 | 4.2014 | 38249.4444 | 563 | 0 | 80 | 9104 | 175 | 9104 | 16 | 9104 | 96 | 0 | 300 | 0 | 6436345.92 | 537427176.2667 | 706.98 | 59031.9833
23 | Khanewal | Ali Sherwan | Rural | 6714 | 390 | 117 | 785538 | 34 | 307 | 2473437.6 | 614 | 4946875.2 | 131 | 879534 | 4.2639 | 28627.75 | 424 | 0 | 80 | 6714 | 175 | 6714 | 16 | 6714 | 96 | 0 | 300 | 0 | 4138509.6 | 300886791 | 616.4 | 44814.8333
24 | Khanewal | OLD M/Rashid | Rural | 6057 | 343 | 102.9 | 623265.3 | 18 | 258.1 | 1875974.04 | 516.2 | 3751948.08 | 72 | 436104 | 4.3187 | 26158.6688 | 361 | 0 | 80 | 6057 | 175 | 6057 | 16 | 6057 | 96 | 0 | 300 | 0 | 2935343.34 | 228556200.825 | 484.62 | 37734.225
25 | Khanewal | Allama Iqbal | Rural | 2574 | 273 | 81.9 | 210810.6 | 66 | 257.1 | 794130.48 | 514.2 | 1588260.96 | 7 | 18018 | 25 | 64350 | 339 | 0 | 80 | 2574 | 175 | 2574 | 16 | 0 | 96 | 0 | 300 | 0 | 1022959.08 | 99789089.4 | 397.42 | 38768.1
26 | Khanewal | Pir Sadiq Shah | Rural | 3888 | 244 | 73.2 | 284601.6 | 173 | 343.8 | 1604033.28 | 687.6 | 3208066.56 | 5 | 19440 | 22 | 85536 | 417 | 0 | 80 | 3888 | 175 | 3888 | 16 | 0 | 96 | 0 | 300 | 0 | 1908074.88 | 198469958.4 | 490.76 | 51046.8
27 | Khanewal | Pir Hajan Shair | Rural | 5152 | 415 | 124.5 | 641424 | 13 | 303.5 | 1876358.4 | 607 | 3752716.8 | 160 | 824320 | 5.4361 | 28006.8444 | 428 | 0 | 80 | 5152 | 175 | 5152 | 16 | 5152 | 96 | 0 | 300 | 0 | 3342102.4 | 228767690.6667 | 648.7 | 44403.6667
28 | Khanewal | Kacha Khuh City | Rural | 6509 | 267 | 80.1 | 521370.9 | 20 | 206.9 | 1616054.52 | 413.8 | 3232109.04 | 33 | 214797 | 56 | 364504 | 287 | 0 | 80 | 6509 | 175 | 6509 | 16 | 6509 | 96 | 0 | 300 | 0 | 2352222.42 | 217360895.1 | 361.38 | 33393.9
29 | Khanewal | Chowk Jamal | Rural | 791 | 153 | 45.9 | 36306.9 | 17 | 124.1 | 117795.72 | 248.2 | 235591.44 | 52 | 41132 | 69 | 54579 | 169 | 1 | 80 | 791 | 175 | 791 | 16 | 791 | 96 | 0 | 300 | 0 | 195234.62 | 17519147.1 | 246.82 | 22148.1
30 | Khanewal | 28/10-R | Rural | 5144 | 211 | 63.3 | 325615.2 | 15 | 162.7 | 1004314.56 | 325.4 | 2008629.12 | 65 | 334360 | 93 | 478392 | 226 | 0 | 80 | 5144 | 175 | 5144 | 16 | 5144 | 96 | 0 | 300 | 0 | 1664289.76 | 150198112.8 | 323.54 | 29198.7
31 | Khanewal | 29/10-R | Rural | 2803 | 204 | 61.2 | 171543.6 | 12 | 154.8 | 520685.28 | 309.6 | 1041370.56 | 55 | 154165 | 67 | 187801 | 216 | 0 | 80 | 2803 | 175 | 2803 | 16 | 2803 | 96 | 0 | 300 | 0 | 846393.88 | 74264924.4 | 301.96 | 26494.8
32 | Khanewal | 81/15-L | Rural | 5275 | 363 | 108.9 | 574447.5 | 28 | 282.1 | 1785693 | 564.2 | 3571386 | 57 | 300675 | 98 | 516950 | 390 | 1 | 80 | 5275 | 175 | 5275 | 16 | 5275 | 96 | 5275 | 300 | 0 | 2660815.5 | 247023502.5 | 504.42 | 46829.1
33 | Khanewal | 88/15-L | Rural | 4885 | 257 | 77.1 | 376633.5 | 22 | 201.9 | 1183537.8 | 403.8 | 2367075.6 | 138 | 674130 | 163 | 796255 | 278 | 1 | 80 | 4885 | 175 | 4885 | 16 | 4885 | 96 | 4885 | 300 | 0 | 2234301.3 | 190929736.5 | 457.38 | 39084.9
34 | Khanewal | 102/15-L | Rural | 2798 | 232 | 69.6 | 194740.8 | 26 | 188.4 | 632571.84 | 376.8 | 1265143.68 | 48 | 134304 | 64 | 179072 | 257 | 1 | 80 | 2798 | 175 | 2798 | 16 | 2798 | 96 | 0 | 300 | 0 | 961616.64 | 87237163.2 | 343.68 | 31178.4
35 | Khanewal | 103/15-L | Rural | 4354 | 253 | 75.9 | 330468.6 | 25 | 202.1 | 1055932.08 | 404.2 | 2111864.16 | 71 | 309134 | 101 | 439754 | 278 | 0 | 80 | 4354 | 175 | 4354 | 16 | 4354 | 96 | 4354 | 300 | 0 | 1695534.68 | 154088495.4 | 389.42 | 35390.1
36 | Khanewal | 24/10-R | Rural | 5973 | 237 | 71.1 | 424680.3 | 29 | 194.9 | 1396965.24 | 389.8 | 2793930.48 | 35 | 209055 | 53 | 316569 | 266 | 0 | 80 | 5973 | 175 | 5973 | 16 | 5973 | 96 | 0 | 300 | 0 | 2030700.54 | 187904009.7 | 339.98 | 31458.9
37 | Khanewal | 54/15-L | Rural | 2937 | 145 | 43.5 | 127759.5 | 11 | 112.5 | 396495 | 225 | 792990 | 48 | 140976 | 69 | 202653 | 156 | 0 | 80 | 2937 | 175 | 2937 | 16 | 2937 | 96 | 0 | 300 | 0 | 665230.5 | 60121858.5 | 226.5 | 20470.5
38 | Kabirwala | KOHI WALA | Rural | 7306 | 279 | 83.7 | 611512.2 | 21 | 216.3 | 1896345.36 | 432.6 | 3792690.72 | 72 | 526032 | 102 | 745212 | 300 | 0 | 80 | 7306 | 175 | 7306 | 16 | 7306 | 96 | 7306 | 300 | 0 | 3033889.56 | 274108699.8 | 415.26 | 37518.3
39 | Kabirwala | KUKAR HATA | Rural | 5603 | 193 | 57.9 | 324413.7 | 24 | 159.1 | 1069724.76 | 318.2 | 2139449.52 | 123 | 689169 | 235 | 1316705 | 217 | 0 | 80 | 5603 | 175 | 5603 | 16 | 5603 | 96 | 5603 | 300 | 0 | 2083307.46 | 208342512.3 | 371.82 | 37184.1
40 | Kabirwala | INYAT PUR | Rural | 3822 | 317 | 95.1 | 363472.2 | 7 | 228.9 | 1049826.96 | 457.8 | 2099653.92 | 159 | 607698 | 198 | 756756 | 324 | 0 | 80 | 3822 | 175 | 3822 | 16 | 3822 | 96 | 3822 | 300 | 0 | 2020997.16 | 172475011.8 | 528.78 | 45126.9
41 | Kabirwala | NAWAN SHEHAR | Rural | 4471 | 906 | 271.8 | 1215217.8 | 98 | 732.2 | 3928399.44 | 1464.4 | 7856798.88 | 9 | 40239 | 26.32 | 117676.72 | 1004 | 0 | 80 | 4471 | 175 | 4471 | 16 | 0 | 96 | 0 | 300 | 0 | 5183856.24 | 482114189.4 | 1159.44 | 107831.4
42 | Kabirwala | MAKHDUM PUR | Rural | 4505 | 168 | 50.4 | 227052 | 15 | 132.6 | 716835.6 | 265.2 | 1433671.2 | 24 | 108120 | 63 | 283815 | 183 | 0 | 80 | 4505 | 175 | 4505 | 16 | 4505 | 96 | 0 | 300 | 0 | 1052007.6 | 103730328 | 233.52 | 23025.6
43 | Kabirwala | ALLAH ABAD | Rural | 4010 | 111 | 33.3 | 133533 | 25 | 102.7 | 494192.4 | 205.4 | 988384.8 | 21 | 84210 | 36 | 144360 | 134 | 2 | 80 | 4010 | 175 | 4010 | 16 | 4010 | 96 | 0 | 300 | 0 | 711935.4 | 68365287 | 177.54 | 17048.7
44 | Kabirwala | INDUSTRIAL | Rural | 3678 | 89 | 26.7 | 98202.6 | 7 | 69.3 | 305862.48 | 138.6 | 611724.96 | 41 | 150798 | 58 | 213324 | 96 | 0 | 80 | 3678 | 175 | 0 | 16 | 3678 | 96 | 0 | 300 | 0 | 554863.08 | 49797545.4 | 150.86 | 13539.3
45 | Kabirwala | 8-KASSI | Rural | 5348 | 319 | 95.7 | 511803.6 | 23 | 246.3 | 1580654.88 | 492.6 | 3161309.76 | 32 | 171136 | 34 | 181832 | 340 | 2 | 80 | 5348 | 175 | 5348 | 16 | 5348 | 96 | 0 | 300 | 0 | 2263594.48 | 202123916.4 | 423.26 | 37794.3
46 | Kabirwala | RAZA ABAD | Rural | 4511 | 345 | 103.5 | 466888.5 | 16 | 257.5 | 1393899 | 515 | 2787798 | 14 | 63154 | 20 | 90220 | 361 | 0 | 80 | 4511 | 175 | 4511 | 16 | 0 | 96 | 0 | 300 | 0 | 1923941.5 | 174081745.5 | 426.5 | 38590.5
47 | Kabirwala | MUST PUR | Rural | 4291 | 279 | 83.7 | 359156.7 | 58 | 253.3 | 1304292.36 | 506.6 | 2608584.72 | 66 | 283206 | 140 | 600740 | 337 | 0 | 80 | 4291 | 175 | 4291 | 16 | 4291 | 96 | 4291 | 300 | 0 | 1946655.06 | 193636953.3 | 453.66 | 45126.3
48 | Kabirwala | NOOR PUR | Rural | 3835 | 314 | 94.2 | 361257 | 25 | 244.8 | 1126569.6 | 489.6 | 2253139.2 | 10 | 38350 | 34 | 130390 | 338 | 1 | 80 | 3835 | 175 | 3835 | 16 | 3835 | 96 | 0 | 300 | 0 | 1526176.6 | 144095523 | 397.96 | 37573.8
49 | Kabirwala | 3-AH | Rural | 4409 | 415 | 124.5 | 548920.5 | 94 | 384.5 | 2034312.6 | 769 | 4068625.2 | 38 | 167542 | 93 | 410037 | 508 | 1 | 80 | 4409 | 175 | 4409 | 16 | 4409 | 96 | 0 | 300 | 0 | 2750775.1 | 270366493.5 | 623.9 | 61321.5
50 | Kabirwala | 13/8-R | Rural | 4108 | 360 | 108 | 443664 | 26 | 278 | 1370428.8 | 556 | 2740857.6 | 18 | 73944 | 55 | 225940 | 385 | 1 | 80 | 4108 | 175 | 4108 | 16 | 4108 | 96 | 0 | 300 | 0 | 1888036.8 | 179338848 | 459.6 | 43656
51 | Kabirwala | Jodh Pur | Rural | 4261 | 187 | 56.1 | 239042.1 | 19 | 149.9 | 766468.68 | 299.8 | 1532937.36 | 9 | 38349 | 19 | 80959 | 205 | 1 | 80 | 4261 | 175 | 4261 | 16 | 4261 | 96 | 0 | 300 | 0 | 1043859.78 | 97550907.9 | 244.98 | 22893.9
52 | Kabirwala | QATAL PUR | Rural | 10369 | 1007 | 302.1 | 3132474.9 | 16 | 720.9 | 8970014.52 | 1441.8 | 17940029.04 | 13 | 134797 | 30.01 | 311173.69 | 1022 | 1 | 80 | 10369 | 175 | 10369 | 16 | 0 | 96 | 0 | 300 | 10369 | 12237286.42 | 1104469588.5 | 1180.18 | 106516.5
53 | Kabirwala | SARAI SIDHU | Rural | 11004 | 1062 | 318.6 | 3505874.4 | 17 | 760.4 | 10040929.92 | 1520.8 | 20081859.84 | 61 | 671244 | 78.17 | 860182.68 | 1078 | 1 | 80 | 11004 | 175 | 11004 | 16 | 11004 | 96 | 0 | 300 | 11004 | 14218048.32 | 1267040174.4 | 1292.08 | 115143.6
54 | Kabirwala | CHOPPER HATA | Rural | 5731 | 593 | 177.9 | 1019544.9 | 26 | 441.1 | 3033532.92 | 882.2 | 6067065.84 | 11 | 63041 | 25 | 143275 | 618 | 1 | 80 | 5731 | 175 | 5731 | 16 | 5731 | 96 | 0 | 300 | 0 | 4116118.82 | 375679085.1 | 718.22 | 65552.1
55 | Kabirwala | AKBAR ABAD | Rural | 6574 | 781 | 234.3 | 1540288.2 | 5 | 551.7 | 4352250.96 | 1103.4 | 8704501.92 | 20 | 131480 | 1.6528 | 10865.3611 | 786 | 0 | 80 | 6574 | 175 | 6574 | 16 | 6574 | 96 | 0 | 300 | 0 | 6024019.16 | 527542901.4667 | 916.34 | 80246.8667
56 | Kabirwala | New Qatal Pur | Rural | 4961 | 912 | 273.6 | 1357329.6 | 1 | 639.4 | 3806476.08 | 1278.8 | 7612952.16 | 16 | 79376 | 1.6667 | 8268.3333 | 913 | 0 | 80 | 4961 | 175 | 4961 | 16 | 0 | 96 | 0 | 300 | 0 | 5243181.68 | 461345218.4 | 1056.88 | 92994.4
57 | Kabirwala | SARDAR PUR | Rural | 6276 | 246 | 73.8 | 463168.8 | 26 | 198.2 | 1492683.84 | 396.4 | 2985367.68 | 56 | 351456 | 126 | 790776 | 272 | 0 | 80 | 6276 | 175 | 6276 | 16 | 6276 | 96 | 6276 | 300 | 0 | 2307308.64 | 227958127.2 | 367.64 | 36322.2
58 | Kabirwala | CHOWKI HIRAJ | Rural | 4471 | 273 | 81.9 | 366174.9 | 8 | 199.1 | 1068211.32 | 398.2 | 2136422.64 | 42 | 187782 | 115 | 514165 | 281 | 0 | 80 | 4471 | 175 | 4471 | 16 | 4471 | 96 | 4471 | 300 | 0 | 1622168.22 | 160133783.1 | 362.82 | 35816.1
59 | Kabirwala | SHER KHAN | Rural | 4577 | 463 | 138.9 | 635745.3 | 29 | 353.1 | 1939366.44 | 706.2 | 3878732.88 | 36 | 164772 | 101 | 462277 | 492 | 0 | 80 | 4577 | 175 | 4577 | 16 | 4577 | 96 | 4577 | 300 | 0 | 2739883.74 | 262367828.7 | 598.62 | 57323.1
60 | Kabirwala | BAQIR PUR | Rural | 4421 | 966 | 289.8 | 1281205.8 | 16 | 692.2 | 3672259.44 | 1384.4 | 7344518.88 | 21 | 92841 | 1.5556 | 6877.1111 | 982 | 0 | 80 | 4421 | 175 | 4421 | 16 | 4421 | 96 | 0 | 300 | 0 | 5046306.24 | 444927376.8667 | 1141.44 | 100639.5333
61 | Kabirwala | Khaliq Wali | Rural | 4069 | 1033 | 309.9 | 1260983.1 | 95 | 818.1 | 3994618.68 | 1636.2 | 7989237.36 | 197 | 801593 | 242 | 984698 | 1128 | 0 | 80 | 4069 | 175 | 4069 | 16 | 4069 | 96 | 4069 | 300 | 4069 | 6057194.78 | 542219070.9 | 1488.62 | 133256.1
62 | Mian Channu | New Kassowal | Rural | 4107 | 137 | 41.1 | 168797.7 | 44 | 139.9 | 689483.16 | 279.8 | 1378966.32 | 66 | 271062 | 258.45 | 1061454.15 | 181 | 0 | 80 | 4107 | 175 | 4107 | 16 | 4107 | 96 | 4107 | 300 | 0 | 1129342.86 | 146931621.3 | 274.98 | 35775.9
63 | Mian Channu | Mamdoot | Rural | 4702 | 147 | 44.1 | 207358.2 | 39 | 141.9 | 800656.56 | 283.8 | 1601313.12 | 62 | 291524 | 278.4 | 1309036.8 | 185 | 1 | 80 | 4702 | 175 | 4702 | 16 | 4702 | 96 | 4702 | 300 | 0 | 1299538.76 | 175243069.8 | 276.38 | 37269.9
64 | Mian Channu | Hamad Bungalow | Rural | 4239 | 131 | 39.3 | 166592.7 | 45 | 136.7 | 695365.56 | 273.4 | 1390731.12 | 41 | 173799 | 272 | 1153008 | 175 | 1 | 80 | 4239 | 175 | 4239 | 16 | 4239 | 96 | 4239 | 300 | 0 | 1035757.26 | 153124125.3 | 244.34 | 36122.7
65 | Mian Channu | Chak-13 | Rural | 3071 | 90 | 27 | 82917 | 45 | 108 | 398001.6 | 216 | 796003.2 | 58 | 178118 | 278 | 853738 | 134 | 1 | 80 | 3071 | 175 | 3071 | 16 | 3071 | 96 | 3071 | 300 | 0 | 659036.6 | 99233223 | 214.6 | 32313
66 | Mian Channu | Chak-6 | Rural | 4004 | 206 | 61.8 | 247447.2 | 8 | 152.2 | 731290.56 | 304.4 | 1462581.12 | 23 | 92092 | 48 | 192192 | 213 | 1 | 80 | 4004 | 175 | 4004 | 16 | 4004 | 96 | 0 | 300 | 0 | 1070829.76 | 100028728.8 | 267.44 | 24982.2
67 | Mian Channu | Munir Abad | Rural | 6099 | 329 | 98.7 | 601971.3 | 9 | 239.3 | 1751388.84 | 478.6 | 3502777.68 | 26 | 158574 | 55 | 335445 | 337 | 1 | 80 | 6099 | 175 | 6099 | 16 | 6099 | 96 | 0 | 300 | 0 | 2511934.14 | 232099274.7 | 411.86 | 38055.3
68 | Mian Channu | Chak 95 | Rural | 6664 | 282 | 84.6 | 563774.4 | 55 | 252.4 | 2018392.32 | 504.8 | 4036784.64 | 34 | 226576 | 67 | 446488 | 336 | 1 | 80 | 6664 | 175 | 6664 | 16 | 6664 | 96 | 0 | 300 | 0 | 2808742.72 | 270687681.6 | 421.48 | 40619.4
69 | Mian Channu | Old Kacha Khu | Rural | 5162 | 158 | 47.4 | 244678.8 | 44 | 154.6 | 957654.24 | 309.2 | 1915308.48 | 50 | 258100 | 90.2 | 465612.4 | 201 | 1 | 80 | 5162 | 175 | 5162 | 16 | 5162 | 96 | 0 | 300 | 0 | 1460433.04 | 143589289.2 | 282.92 | 27816.6
70 | Mian Channu | Chak-98 | Rural | 5483 | 149 | 44.7 | 245090.1 | 50 | 154.3 | 1015232.28 | 308.6 | 2030464.56 | 62 | 339946 | 147 | 806001 | 198 | 1 | 80 | 5483 | 175 | 5483 | 16 | 5483 | 96 | 5483 | 300 | 0 | 1600268.38 | 170923203.9 | 291.86 | 31173.3
71 | Mian Channu | Vehari Road | Rural | 7993 | 356 | 106.8 | 853652.4 | 37 | 286.2 | 2745115.92 | 572.4 | 5490231.84 | 98 | 783314 | 160 | 1278880 | 392 | 1 | 80 | 7993 | 175 | 7993 | 16 | 7993 | 96 | 7993 | 300 | 0 | 4382082.32 | 408707667.6 | 548.24 | 51133.2
72 | Mian Channu | Venjori | Rural | 7006 | 350 | 105 | 735630 | 16 | 261 | 2194279.2 | 522 | 4388558.4 | 78 | 546468 | 14 | 98084 | 365 | 1 | 80 | 7006 | 175 | 7006 | 16 | 7006 | 96 | 0 | 300 | 0 | 3476377.2 | 271405434 | 496.2 | 38739
73 | Mian Channu | Chak-135 | Rural | 195 | 100 | 30 | 5850 | 8 | 78 | 18252 | 156 | 36504 | 216 | 42120 | 300 | 58500 | 107 | 1 | 80 | 195 | 175 | 195 | 16 | 195 | 96 | 195 | 300 | 0 | 66222 | 5717790 | 339.6 | 29322
74 | Mian Channu | Chak-126 | Rural | 4545 | 15 | 4.5 | 20452.5 | 33 | 43.5 | 237249 | 87 | 474498 | 11 | 49995 | 15.3 | 69538.5 | 47 | 1 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 307696.5 | 32703547.5 | 67.7 | 7195.5
75 | Mian Channu | Rehman Garh | Rural | 5954 | 400 | 120 | 714480 | 19 | 299 | 2136295.2 | 598 | 4272590.4 | 29 | 172666 | 70.78 | 421424.12 | 418 | 1 | 80 | 5954 | 175 | 5954 | 16 | 5954 | 96 | 0 | 300 | 0 | 3023441.2 | 283784311.2 | 507.8 | 47662.8
76 | Mian Channu | Tulamba Old A/H | Rural | 2267 | 139 | 41.7 | 94533.9 | 10 | 107.3 | 291898.92 | 214.6 | 583797.84 | 341 | 773047 | 354.5 | 803651.5 | 148 | 1 | 80 | 2267 | 175 | 2267 | 16 | 2267 | 96 | 2267 | 300 | 0 | 1159479.82 | 83530562.1 | 511.46 | 36846.3
77 | Mian Channu | New Kacha Khu | Rural | 3819 | 86 | 25.8 | 98530.2 | 20 | 80.2 | 367540.56 | 160.4 | 735081.12 | 42 | 160398 | 61 | 232959 | 105 | 1 | 80 | 3819 | 175 | 3819 | 16 | 3819 | 96 | 0 | 300 | 0 | 626468.76 | 58377997.8 | 164.04 | 15286.2
78 | Mian Channu | Mohsinwal | Rural | 6623 | 138 | 41.4 | 274192.2 | 58 | 154.6 | 1228698.96 | 309.2 | 2457397.92 | 64 | 423872 | 100.1 | 662962.3 | 195 | 1 | 80 | 6623 | 175 | 6623 | 16 | 6623 | 96 | 6623 | 300 | 0 | 1926763.16 | 188044189.8 | 290.92 | 28392.6
79 | Mian Channu | I/Estate | Rural | 38 | 20 | 6 | 228 | 7 | 21 | 957.6 | 42 | 1915.2 | 6 | 228 | 20.55 | 780.9 | 26 | 1 | 80 | 0 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 1413.6 | 162450 | 37.2 | 4275
80 | Mian Channu | Dullo Bungalow | Rural | 4331 | 160 | 48 | 207888 | 49 | 161 | 836749.2 | 322 | 1673498.4 | 1014 | 4391634 | 349 | 1511519 | 208 | 1 | 80 | 4331 | 175 | 4331 | 16 | 4331 | 96 | 4331 | 300 | 0 | 5436271.2 | 191724708 | 1255.2 | 44268
81 | Mian Channu | Old Kassowal | Rural | 7901 | 141 | 42.3 | 334212.3 | 39 | 137.7 | 1305561.24 | 275.4 | 2611122.48 | 75 | 592575 | 307.4 | 2428767.4 | 180 | 0 | 80 | 7901 | 175 | 7901 | 16 | 7901 | 96 | 7901 | 300 | 0 | 2232348.54 | 303396029.7 | 282.54 | 38399.7
82 | Mian Channu | New Mohsinwal | Rural | 4767 | 142 | 42.6 | 203074.2 | 50 | 149.4 | 854627.76 | 298.8 | 1709255.52 | 67 | 319389 | 36.5 | 173995.5 | 192 | 0 | 80 | 4767 | 175 | 4767 | 16 | 4767 | 96 | 0 | 300 | 0 | 1377090.96 | 113604283.8 | 288.88 | 23831.4
83 | Mian Channu | Ravi | Rural | 5897 | 48 | 14.4 | 84916.8 | 37 | 70.6 | 499593.84 | 141.2 | 999187.68 | 15 | 88455 | 19.05 | 112337.85 | 85 | 0 | 80 | 5897 | 175 | 0 | 16 | 0 | 96 | 0 | 300 | 0 | 672965.64 | 66946282.2 | 114.12 | 11352.6
84 | Mian Channu | Bodla | Rural | 4348 | 189 | 56.7 | 246531.6 | 50 | 182.3 | 951168.48 | 364.6 | 1902336.96 | 29 | 126092 | 68.1 | 296098.8 | 239 | 0 | 80 | 4348 | 175 | 4348 | 16 | 4348 | 96 | 0 | 300 | 0 | 1323792.08 | 132645740.4 | 304.46 | 30507.3
85 | Mian Channu | Tulamba M/C | Rural | 6086 | 120 | 36 | 219096 |  | 84 | 613468.8 | 168 | 1226937.6 |  | 0 |  | 0 | 120 | 0 | 80 | 6086 | 175 | 6086 | 16 | 0 | 96 | 0 | 300 | 0 | 832564.8 | 74273544 | 136.8 | 12204
86 | Mian Channu | Chak-8BR | Rural | 3617 | 90 | 27 | 97659 | 35 | 98 | 425359.2 | 196 | 850718.4 | 49 | 177233 | 210 | 759570 | 124 | 1 | 80 | 3617 | 175 | 3617 | 16 | 3617 | 96 | 3617 | 300 | 0 | 700251.2 | 96910281 | 193.6 | 26793
87 | Mian Channu | Mamo Shair | Rural | 4443 | 418 | 125.4 | 557152.2 | 14 | 306.6 | 1634668.56 | 613.2 | 3269337.12 | 51 | 226593 | 69.42 | 308433.06 | 431 | 1 | 80 | 4443 | 175 | 4443 | 16 | 4443 | 96 | 0 | 300 | 0 | 2418413.76 | 216337667.4 | 544.32 | 48691.8
88 | Mian Channu | Chab Banglow | Rural | 3568 | 51 | 15.3 | 54590.4 | 10 | 45.7 | 195669.12 | 91.4 | 391338.24 | 47 | 167696 | 41 | 146288 | 60 | 1 | 80 | 0 | 175 | 0 | 16 | 3568 | 96 | 0 | 300 | 0 | 417955.52 | 32421345.6 | 117.14 | 9086.7
|  | TOTAL |  | 441110 | 20573 | 7724.7 | 43300090.2 | 2131 | 20591.3 | 136547373.36 | 41182.6 | 273094746.72 | 6571 | 34309896 | 8948.9613 | 39669976.6267 | 28279 | 37 | 80 | 426441 | 175 | 416866 | 16 | 338758 | 96 | 139110 | 300 | 25442 | 214157359.56 | 18895783671.4 | 485.4965 | 42836.8971

## 11-KV Company
Statement of 11-KV MEPCO Consumers For 2020-21
11-KV
|  | A |  | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S=(B+C+E) | T=Bx3+Dx60+Fx60 | U=S/A | V=T/A
Sr. No. | Company | Circle | No. of Consumer | Consumers Annual Total Short Interruptions | Consumers Annual Total Unplanned Long Interruptions | Consumers Annual Long Un-planned Interruptions Duration (Hrs) | Consumers Annual Total No. of Planned Interruptions | Consumers Annual Planned Interruptions Duration (Hrs) | Un-Planned Interruptions Restored within 10 Hrs. | Restored after 10 Hrs | Pmt No. of un-planned interruptions Annual (GS2) | No. of consumers whose un-planned power supply interruptions exceeded Pmt Limit (GS2) | Max Pmt Agrt: duration Unplanned Annual Hrs (GS3) | No. of Consumers who exceeded agrt: limit (GS3) | Max Omt: No. of Planned interruptions (GS4) | No. of consumers who exceeded limit of Agrt: planned interruptions (GS4) | Max Pmt agrt: duration planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short Duration GS6) | No. of Consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: sume of all consumers interruptions Duration (Mint:) | SAIFI | SAIDI
1 | MEPCO | Multan | 80 | 2584 | 755 | 2633.23 | 697 | 2626.5 | 3339 | 0 | 30 | 48 | 44 | 16 | 8 | 30 | 64 | 14 | 140 | 0 | 4036 | 323335.8 | 50.45 | 4041.6975
2 |  | D.G Khan | 24 | 947 | 185 | 598 | 211 | 0 | 1253 | 12 | 30 | 12 | 44 | 5 | 8 | 8 | 64 | 3 | 140 | 0 | 1343 | 38721 | 55.9583 | 1613.375
3 |  | Vehari | 8 | 72 | 23 | 48.7674 | 17 | 28.6181 | 111 | 2 | 30 | 1 | 44 | 0 | 8 | 2 | 64 | 0 | 140 | 1 | 112 | 4859.125 | 14 | 607.3906
4 |  | Bahawalpur | 34 | 909 | 221 | 590.4322 | 341.2 | 575.521 | 1130 | 0 | 30 | 14 | 44 | 5 | 8 | 10 | 64 | 1 | 140 | 1 | 1471.2 | 72684.1917 | 43.2706 | 2137.7703
5 |  | Sahiwal | 33 | 601 | 235 | 3.05 | 200 | 0 | 838 | 14 | 30 | 7 | 44 | 29 | 8 | 5 | 64 | 31 | 140 | 1 | 1036 | 1986 | 31.3939 | 60.1818
6 |  | R.Y Khan | 25 | 732 | 98 | 53.36 | 159 | 691.5 | 830 | 0 | 30 | 7 | 44 | 0 | 8 | 8 | 64 | 3 | 140 | 1 | 989 | 46887.6 | 39.56 | 1875.504
7 |  | Muzaffargarh | 43 | 837 | 160 | 717 | 297 | 1013 | 995 | 2 | 30 | 9 | 44 | 8 | 8 | 14 | 64 | 3 | 140 | 0 | 1294 | 106311 | 30.093 | 2472.3488
8 |  | Bahawal Nagar | 7 | 590 | 80 | 44.3514 | 125 | 20.2278 | 669 | 1 | 30 | 5 | 44 | 0 | 8 | 4 | 64 | 0 | 140 | 2 | 795 | 5644.75 | 113.5714 | 806.3929
9 |  | Khanewal | 24 | 363 | 84 | 513.62 | 94 | 363.39 | 444 | 5 | 30 | 7 | 44 | 4 | 8 | 4 | 64 | 1 | 140 | 0 | 541 | 53709.6 | 22.5417 | 2237.9
|  |  | 278 | 7635 | 1841 | 5201.811 | 2141.2 | 5318.7568 | 9609 | 36 | 30 | 110 | 44 | 67 | 8 | 85 | 64 | 56 | 140 | 6 | 11617.2 | 654139.0667 | 41.7885 | 2353.0182

## 220 Urban
Statement of 400/220 V MEPCO Consumers For 2020-21
Urban
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Company | Circle |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | MEPCO | Multan | Urban | 612214 | 15867 | 4760 | 26822398 | 5135 | 16242 | 110142792 | 16242 | 110142792 | 3751 | 20974934 | 8339 | 42840721 | 21002 | 171 | 60 | 582122 | 88 | 517516 | 16 | 333210 | 80 | 173521 | 275 | 0 | 157940124 | 9259477969 | 258 | 15125
2 |  | D.G Khan | Urban | 204135 | 9269 | 2780.7 | 17806630.5 | 1765 | 8253.3 | 62954625 | 8253.3 | 62954625 | 3835 | 19081375 | 5872 | 31976525 | 11030 | 4 | 60 | 204135 | 88 | 182856 | 16 | 203748 | 80 | 154046 | 275 | 0 | 99842630.5 | 5749288891.5 | 489.101 | 28164.1506
3 |  | Vehari | Urban | 122985 | 2465 | 1106.1 | 6108410.7 | 261 | 2993.9 | 19748408.76 | 2993.9 | 19748408.76 | 712 | 6963292 | 2558 | 13275662 | 4100 | 0 | 60 | 112911 | 88 | 83158 | 16 | 118874 | 80 | 72956 | 275 | 0 | 32820111.46 | 1999769477.7 | 266.8627 | 16260.2714
4 |  | Bahawalpur | Urban | 409192 | 7400 | 2220 | 12025609.2 | 2770 | 7950 | 51644188.56 | 7950 | 51644188.56 | 2877 | 13315148 | 4065.75 | 19292033.65 | 9956 | 9 | 60 | 338727 | 88 | 258669 | 16 | 117217 | 80 | 87446 | 275 | 0 | 76984945.76 | 4292250160.2 | 188.1389 | 10489.575
5 |  | Sahiwal | Urban | 177622 | 3929 | 1307.1 | 6523701 | 1097 | 4202.9 | 24430906.8 | 4202.9 | 24430906.8 | 2070 | 11010704 | 4225.55 | 12955735.48 | 5503 | 7 | 60 | 152045 | 88 | 95751 | 16 | 142750 | 80 | 78609 | 275 | 0 | 41965311.8 | 2262769639.8 | 236.2619 | 12739.242
6 |  | R.Y Khan | Urban | 231418 | 2220 | 666 | 4359155.1 | 951 | 2505 | 19618262.28 | 2505 | 19618262.28 | 889 | 5233562 | 2666 | 15536650 | 3161 | 10 | 60 | 188611 | 88 | 107646 | 16 | 154832 | 80 | 67515 | 275 | 0 | 29210979.38 | 2122372202.1 | 126.226 | 9171.163
7 |  | Muzaffargarh | Urban | 157577 | 230 | 1101 | 8261724.3 | 109 | 3285 | 29415352.44 | 3285 | 29415352.44 | 375 | 11328132 | 629 | 17584746 | 4386 | 0 | 60 | 157515 | 88 | 126901 | 16 | 157577 | 80 | 157577 | 275 | 0 | 49005208.74 | 2844791079.3 | 310.9921 | 18053.3395
8 |  | Bahawal Nagar | Urban | 215983 | 5815 | 1744.5 | 16461600.3 | 526 | 4596.5 | 51269909.64 | 4596.5 | 51269909.64 | 1501 | 10974066 | 0 | 25715857 | 6340 | 1 | 60 | 196099 | 88 | 164549 | 16 | 191310 | 80 | 215983 | 275 | 0 | 78705575.94 | 4668530799.3 | 364.4063 | 21615.2697
9 |  | Khanewal | Urban | 100966 | 3546 | 712.2 | 4774749.9 | 219 | 1923.8 | 15374947.32 | 1923.8 | 15374947.32 | 928 | 7010979 | 2119.0072 | 15774226.5794 | 4119 | 41 | 60 | 93454 | 88 | 85994 | 16 | 71324 | 80 | 52886 | 275 | 0 | 27160676.22 | 1883274683.6667 | 269.0081 | 18652.5631
|  | TOTAL |  | 2232092 | 50741 | 16397.6 | 103143979 | 12833 | 51952.4 | 384599392.8 | 51952.4 | 384599392.8 | 16938 | 105892192 | 30474.3072 | 194952156.7094 | 69597 | 243 | 60 | 2025619 | 88 | 1623040 | 16 | 1490842 | 80 | 1060539 | 275 | 0 | 593635563.8 | 35082524902.5667 | 265.9548 | 15717.3293

## 220 Rural
Statement of 400/220 V MEPCO Consumers For 2020-21
Rural
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Company | Circle |  | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual9GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | MEPCO | Multan | Rural | 468756 | 32849 | 9854.7 | 53819409.3 | 6898 | 29892.3 | 194346172.44 | 59784.6 | 388692344.88 | 5665 | 29555830 | 8259.2222 | 43615759.2888 | 39744 | 4 | 80 | 452126 | 175 | 444536 | 16 | 285271 | 96 | 120308 | 300 | 13918 | 277721411.74 | 26099944478.025 | 592.4648 | 55679.1689
2 |  | D.G Khan | Rural | 345573 | 53570 | 16071 | 83010674.7 | 4385 | 41884 | 260918053.56 | 83768 | 521836107.12 | 25503 | 111786995 | 31553 | 140391406 | 62806 | 65 | 80 | 332927 | 175 | 332135 | 16 | 334557 | 96 | 296023 | 300 | 107224 | 455715723.26 | 39982682811.3 | 1318.7249 | 115699.6722
3 |  | Vehari | Rural | 442791 | 29453 | 9963 | 51335287.8 | 1299 | 24774 | 153773925.84 | 49548 | 307547851.68 | 6913 | 33515197 | 11097 | 47062260 | 34737 | 0 | 80 | 436345 | 175 | 431429 | 16 | 390701 | 96 | 183089 | 300 | 0 | 238624410.64 | 21430612564.2 | 538.9098 | 48398.9344
4 |  | Bahawalpur | Rural | 533227 | 24732 | 7419.6 | 33289177.5 | 5127 | 22439.4 | 122132211 | 44878.8 | 244264422 | 0 | 22363024 | 9530.55 | 39926963.75 | 36644 | 21 | 80 | 511907 | 175 | 478066 | 16 | 211146 | 96 | 134336 | 300 | 0 | 177784412.5 | 17151350677.5 | 333.4122 | 32165.1955
5 |  | Sahiwal | Rural | 525289 | 40604 | 12945.3 | 61075507.8 | 2251.4 | 32644.1 | 185943324.72 | 65288.2 | 371886649.44 | 4959 | 32335909 | 8625.37 | 43825836.3 | 45565 | 24 | 80 | 524908 | 175 | 517962 | 16 | 423934 | 96 | 200616 | 300 | 0 | 279354741.52 | 25125975667.8 | 531.8115 | 47832.6705
6 |  | R.Y Khan | Rural | 535011 | 18764 | 5629.2 | 32483095.8 | 3696 | 16408.8 | 114971391.84 | 32817.6 | 229942783.68 | 26516 | 121534886 | 29711 | 140588166 | 24510 | 52 | 80 | 519868 | 175 | 502872 | 16 | 413045 | 96 | 272816 | 300 | 0 | 268989373.64 | 22329306268.2 | 502.7735 | 41736.1629
7 |  | Muzaffargarh | Rural | 650212 | 2551 | 12722.4 | 85748799.9 | 1032 | 34309.6 | 276763468.92 | 68619.2 | 553526937.84 | 783 | 41144416 | 1413 | 75867023 | 53089 | 0 | 80 | 645052 | 175 | 640871 | 16 | 650082 | 96 | 618258 | 300 | 29601 | 403656684.82 | 38020884050.1 | 620.8078 | 58474.5961
8 |  | Bahawal Nagar | Rural | 343848 | 16903 | 5070.9 | 29674693.8 | 3144 | 14976.1 | 100240818.24 | 29952.2 | 200481636.48 | 4846 | 27971290 | 8087.5 | 45852879.7 | 20047 | 0 | 80 | 328596 | 175 | 307036 | 16 | 322685 | 96 | 199587 | 300 | 0 | 157886802.04 | 14869095052.2 | 459.1762 | 43243.221
9 |  | Khanewal | Rural | 441110 | 20573 | 7724.7 | 43300090.2 | 2131 | 20591.3 | 136547373.36 | 41182.6 | 273094746.72 | 6571 | 34309896 | 8948.9613 | 39669976.6267 | 28279 | 37 | 80 | 426441 | 175 | 416866 | 16 | 338758 | 96 | 139110 | 300 | 25442 | 214157359.56 | 18895783671.4 | 485.4965 | 42836.8971
|  | TOTAL |  | 4285817 | 239999 | 87400.8 | 473736736.8 | 29963.4 | 237919.6 | 1545636739.92 | 475839.2 | 3091273479.84 | 81756 | 454517443 | 117225.6035 | 616800270.6654 | 345421 | 203 | 80 | 4178170 | 175 | 4071773 | 16 | 3370179 | 96 | 2164143 | 300 | 176185 | 2473890919.72 | 223905635240.725 | 577.2274 | 52243.3961

## MEPCO
Statement of 400/220 V MEPCO Consumers For 2020-21
|  |  | A | A1 | B | B1=(BX0.3) | B2=(B1XA1) | C | C1=BX0.7+C) | C2=C1XA1X1.2) | D | D1=DXA1X1.2) | E | F=EXA1 | G | G1=GXA1 | H | I=C1-H | J | K | L | M | N | O | P | Q | R | S | T=(B2+C2+F) | U=B2X3+D1X60+G1X60) | V=T/AI | W=U/A1
Sr. No. | Company | Circle | Urban + Rural | Connections | Annual feeder interruptions below 20 Min | Annual Feeder Short Interruptions | Consumers Annual Total Short Interruptions | Annual Feeder interruptions Above 20 Min | Annual Feeder un-planned Long Interruptions | Consumers Annual Total unplanned long interruptions including 20% LT interruptions | Feeder Annual long unplanned interruptions duration (Hrs) U = C1x1 R = C1x2 | Consumers Annual long unplanned interruptions Duration Hrs including 20% LT Interruptions | No. of Annual planned interruptions of Feeder | Consumers Annual Total No. of Planned interruptions | Feeders Annual planned interruptions duration (Hrs) | Consumer Annual planned interruptions Duration (Hrs) | Un-planned interruptions restored within 10/16 Hrs | Restored After 10/16-Hrs | Pmt No. of un-planned interruptions Annual(GS2) | No. of consumers whose unplanned power supply interruption exceeded pmt limit (GS2) | Max: Pmt Agrt: duration un-planned Annual Hrs (GS3) | No. of consumers who exceeded Agrt: limit (GS3) | Max Pmt No. of Planned interruptions 9GS4) | No. of Consumers who exceeded limit of agrt: planned interruptions (GS4) | Max: Pmt Agrt:planned Annual Hrs (GS5) | No. of consumers who exceeded agrt: limit (GS5) | Max: Pmt Short durations (GS6) | No. of consumers who exceeded limit (GS6) | Total Interruptions Annual | Annual Agrt: Sum of all consumers interruptions duration (Min) | SAIFI | SAIDI
1 | MEPCO | Multan | Urban + Rural | 1080970 | 48716 | 14614.7 | 80641807.3 | 12033 | 46134.3 | 304488964.44 | 76026.6 | 498835136.88 | 9416 | 50530764 | 16598.2222 | 86456480.2887 | 60746 | 175 |  | 1034248 |  | 962052 |  | 618481 |  | 293829 |  | 13918 | 435661535.74 | 35359422447.025 | 850.4648 | 70804.1689
2 |  | D.G Khan |  | 549708 | 62839 | 18851.7 | 100817305.2 | 6150 | 50137.3 | 323872678.56 | 92021.3 | 584790732.12 | 29338 | 130868370 | 37425 | 172367931 | 73836 | 69 |  | 537062 |  | 514991 |  | 538305 |  | 450069 |  | 107224 | 555558353.76 | 45731971702.8 | 1807.8259 | 143863.8228
3 |  | Vehari |  | 565776 | 31918 | 11069.1 | 57443698.5 | 1560 | 27767.9 | 173522334.6 | 52541.9 | 327296260.44 | 7625 | 40478489 | 13655 | 60337922 | 38837 | 0 |  | 549256 |  | 514587 |  | 509575 |  | 256045 |  | 0 | 271444522.1 | 23430382041.9 | 805.7725 | 64659.2058
4 |  | Bahawalpur |  | 942419 | 32132 | 9639.6 | 45314786.7 | 7897 | 30389.4 | 173776399.56 | 52828.8 | 295908610.56 | 2877 | 35678172 | 13596.3 | 59218997.4 | 46600 | 30 |  | 850634 |  | 736735 |  | 328363 |  | 221782 |  | 0 | 254769358.26 | 21443600837.7 | 521.5512 | 42654.7704
5 |  | Sahiwal |  | 702911 | 44533 | 14252.4 | 67599208.8 | 3348.4 | 36847 | 210374231.52 | 69491.1 | 396317556.24 | 7029 | 43346613 | 12850.92 | 56781571.78 | 51068 | 31 |  | 676953 |  | 613713 |  | 566684 |  | 279225 |  | 0 | 321320053.32 | 27388745307.6 | 768.0734 | 60571.9125
6 |  | R.Y Khan |  | 766429 | 20984 | 6295.2 | 36842250.9 | 4647 | 18913.8 | 134589654.12 | 35322.6 | 249561045.96 | 27405 | 126768448 | 32377 | 156124816 | 27671 | 62 |  | 708479 |  | 610518 |  | 567877 |  | 340331 |  | 0 | 298200353.02 | 24451678470.3 | 628.9996 | 50907.3259
7 |  | Muzaffargarh |  | 807789 | 2781 | 13823.4 | 94010524.2 | 1141 | 37594.6 | 306178821.36 | 71904.2 | 582942290.28 | 1158 | 52472548 | 2042 | 93451769 | 57475 | 0 |  | 802567 |  | 767772 |  | 807659 |  | 775835 |  | 29601 | 452661893.56 | 40865675129.4 | 931.7999 | 76527.9356
8 |  | Bahawal Nagar |  | 559831 | 22718 | 6815.4 | 46136294.1 | 3670 | 19572.6 | 151510727.88 | 34548.7 | 251751546.12 | 6347 | 38945356 | 8087.5 | 71568736.7 | 26387 | 1 |  | 524695 |  | 471585 |  | 513995 |  | 415570 |  | 0 | 236592377.98 | 19537625851.5 | 823.5825 | 64858.4907
9 |  | Khanewal |  | 542076 | 24119 | 8436.9 | 48074840.1 | 2350 | 22515.1 | 151922320.68 | 43106.4 | 288469694.04 | 7499 | 41320875 | 11067.9685 | 55444203.2061 | 32398 | 78 |  | 519895 |  | 502860 |  | 410082 |  | 191996 |  | 25442 | 241318035.78 | 20779058355.0667 | 754.5046 | 61489.4602
|  | TOTAL |  | 6517909 | 290740 | 103798.4 | 576880715.8 | 42796.4 | 289872 | 1930236132.72 | 527791.6 | 3475872872.64 | 98694 | 560409635 | 147699.9107 | 811752427.3749 | 415018 | 446 |  | 6203789 |  | 5694813 |  | 4861021 |  | 3224682 |  | 176185 | 3067526483.52 | 258988160143.292 | 470.6305 | 39734.8536
`

## Form1
Form-1
CONSUMER SERVICES AND SYSTEM PERFORMANCE FOR 2020-21
Guaranteed Standards Un-Planned Power Supply Interruptions
Sheet 1
2020-21
Consumer Supply Voltage | Total Number of unplanned consumer Power Supply Interruptions | Number of Unplanned Consumer Power Supply Interruptions (GSIU) |  | Number of Unplanned Consumer Power Supply Interruptions (GSIR) |  | Maximum Permitted Number of Unplanned Power Supply Interruptions for each Individual Consumer per annum (GS2) | Number of Consumers whose number of Unplanned Power Supply Interruptions exceeded the maximum limit of (GS2) | Maximum Power Supply Interruption aggregate duration (Hours) for each individual consumer per annum (GS3) | Number of consumer whose aggregate Planned Power Supply Interruption duration exceeded the Maximum limit of (GS3)
|  | Restored within 10 Hrs | Extend Beyond 10 Hrs | Restored within 16 Hrs | Extend Beyond 16 Hrs
220 KV | - | - | - | - | - | 6 | - | 26 | -
132 KV | - | - | - | - | - | 6 | - | 26 | -
66 KV | - | - | - | - | - | 6 | - | 26 | -
33 KV | - | - | - | - | - | 30 | - | 44 | -
11 KV | 9476 | - | - | 9476 | - | 30 | 110 | 44 | 67
400/230 V Urban | 487743371.8 | 487743371.8 | - | - | - | 60 | 2025619 | 88 | 1623040
400/230 V Rural | 2019373476.72 | - | - | 2019373476.72 | - | 80 | 4178170 | 175 | 4071773
2019-20
Consumer Supply Voltage | Total Number of unplanned consumer Power Supply Interruptions | Number of Unplanned Consumer Power Supply Interruptions (GSIU) |  | Number of Unplanned Consumer Power Supply Interruptions (GSIR) |  | Maximum Permitted Number of Unplanned Power Supply Interruptions for each Individual Consumer per annum (GS2) | Number of Consumers whose number of Unplanned Power Supply Interruptions exceeded the maximum limit of (GS2) | Maximum Power Supply Interruption aggregate duration (Hours) for each individual consumer per annum (GS3) | Number of consumer whose aggregate Planned Power Supply Interruption duration exceeded the Maximum limit of (GS3)
|  | Restored within 10 Hrs | Extend Beyond 10 Hrs | Restored within 16 Hrs | Extend Beyond 16 Hrs
220 KV | - | - | - | - | - | 6 | - | 26 | -
132 KV | - | - | - | - | - | 6 | - | 26 | -
66 KV | - | - | - | - | - | 6 | - | 26 | -
33 KV | - | - | - | - | - | 30 | - | 44 | -
11 KV | 8633 | - | - | 8633 | - | 30 | 97 | 44 | 0
400/230 V Urban | 493411207.38 | 493411207.38 | - | - | - | 60 | 2042138 | 88 | 1768547
400/230 V Rural | 1844708473.68 | - | - | 1844708473.68 | - | 80 | 4164667 | 175 | 4012927

## Form2
Form-2
CONSUMER SERVICES AND SYSTEM PERFORMANCE FOR 2020-21
Guaranteed Standards Un-Planned Power Supply Interruptions
Sheet 2
2020-21
Consumer Supply Voltage | Maximum Permitted Number of Planned Power Supply Interruptions for each Individual Consumer per annum (GS4) | Number of Consumers whose number of Planned Power Supply Interruptions exceeded the maximum limit of (GS4) | Maximum Power Supply Interruption aggregate duration (Hours) for each individual consumer per annum (GS5) | Number of consumer whose aggregate Planned Power Supply Interruption duration exceeded the Maximum limit of (GS5)
220 KV | 4 | - | 36 | -
132 KV | 4 | - | 36 | -
66 KV | 4 | - | 36 | -
33 KV | 8 | - | 64 | -
11 KV | 8 | 85 | 64 | 56
400/230 V Urban | 16 | 1490842 | 80 | 1060539
400/230 V Rural | 16 | 3370179 | 96 | 2164143
2019-20
Consumer Supply Voltage | Maximum Permitted Number of Planned Power Supply Interruptions for each Individual Consumer per annum (GS4) | Number of Consumers whose number of Planned Power Supply Interruptions exceeded the maximum limit of (GS4) | Maximum Power Supply Interruption aggregate duration (Hours) for each individual consumer per annum (GS5) | Number of consumer whose aggregate Planned Power Supply Interruption duration exceeded the Maximum limit of (GS5)
220 KV | 4 | - | 36 | -
132 KV | 4 | - | 36 | -
66 KV | 4 | - | 36 | -
33 KV | 8 | - | 64 | -
11 KV | 8 | 25 | 64 | 8
400/230 V Urban | 16 | 513730 | 80 | 238074
400/230 V Rural | 16 | 867448 | 96 | 226844

## Form3
Form-3
CONSUMER SERVICES AND SYSTEM PERFORMANCE FOR 2020-21
Guaranteed Standards Planned Power Supply Interruptions
Sheet 3
2020-21
Consumer Supply Voltage | Maximum Permitted Number of short duration Power Supply Interruptions for each Individual Consumer per annum (GS6) | Number of Consumers whose short duration Power Supply Interruptions exceeded the maximum limit of (GS6)
132/66 KV | 4 | -
33/11 KV | 140 | 6
400/230 V Urban | 275 | 0
400/230 V Rural | 300 | 176185
2019-20
Consumer Supply Voltage | Maximum Permitted Number of short duration Power Supply Interruptions for each Individual Consumer per annum (GS6) | Number of Consumers whose short duration Power Supply Interruptions exceeded the maximum limit of (GS6)
132/66 KV | 4 | -
33/11 KV | 140 | 2
400/230 V Urban | 275 | 15416
400/230 V Rural | 300 | 83715

## Form4
Form-4
CONSUMER SERVICES AND SYSTEM PERFORMANCE FOR 2020-21
Over all Standards - Average Power Supply Interruptions
Sheet 4
2020-21
Consumer Supply Voltage | Total number of consumer served by the distribution company in a year | Total number of consumer Power Supply Interruption** | SAIFI (OSI) (4) = (3) / (2) | Aggregate Sum of all consumer Power of Supply Interruption Duration in Minutes*** | SAIDI (OS2) (6) =(5)/(2)
220 KV | 1 | - | 0 | - | 0
132 KV | 10 | 113 | 11.3 | 18423 | 1842.3
66 KV | - | - | 0 | - | 0
33 KV | - | - | 0 | - | 0
11 KV | 287 | 11617.2 | 40.478 | 654139.0667 | 2279.2302
400/230 V | 6517909 | 3067526483.52 | 470.6305 | 258988160143.292 | 39734.8536
2019-20
Consumer Supply Voltage | Total number of consumer served by the distribution company in a year | Total number of consumer Power Supply Interruption** | SAIFI (OSI) (4) = (3) / (2) | Aggregate Sum of all consumer Power of Supply Interruption Duration in Minutes*** | SAIDI (OS2) (6) =(5)/(2)
220 KV | 1 | - | 0 | - | 0
132 KV | 8 | - | 0 | - | 0
66 KV | - | - | 0 | - | 0
33 KV | - | - | 0 | - | 0
11 KV | 278 | 9450 | 33.9928 | 221934 | 798.3237
400/230 V | 6398735 | 2405899481.06 | 375.9961 | 204262162301.5 | 31922.2725

## Form5
Form-5
CONSUMER SERVICES AND SYSTEM PERFORMANCE FOR 2020-21
Guaranteed Standards - Time Frame for New Connections
2020-21
Eligible Consumer's New Power Supply Connection requirements Voltage and Load level Specific | Maximum* Time Period for Provision of new Connection (Clandar days) (Overall Standard-3 (OS3) | Total Number of Eligible consumers who applied for a new connection | Total Number of eligible consumers who applied for a new connection and were connected with in maximum permitted time period of OS3 | Total Number eligible consumers who applied for a new connection but did not receive connection within the maximum permitted time period of OS3 | Remarks
Voltage level upto 400 V and load upto 15 KW (Urban) | 30 | 325423 | 310410 | 15013 | 1- Due to meters & cable. 2-Due to transformers. 3.Due to poles. 3. Civil Suit / Right of way by consumer.
Voltage level upto 400 V and load upto 15 KW (Rural) | 45 | 20055 | 19110 | 945
Voltage level upto 400 V and load upto 15 KW but not exceeding 70 KW | 53 | 1997 | 1902 | 95
Voltage level upto 400 V and load above 70 KW but not exceeding 500 KW | 73 | 5237 | 5012 | 225
Voltage level upto 11 KV or 33 KV and load above 500 KW but not exceeding 5000 KW | 106 | 0 | 0 | 0
Voltage level 166 KV and above for all load | 496 | 0 | 0 | 0
2019-20
Eligible Consumer's New Power Supply Connection requirements Voltage and Load level Specific | Maximum* Time Period for Provision of new Connection (Clandar days) (Overall Standard-3 (OS3) | Total Number of Eligible consumers who applied for a new connection | Total Number of eligible consumers who applied for a new connection and were connected with in maximum permitted time period of OS3 | Total Number eligible consumers who applied for a new connection but did not receive connection within the maximum permitted time period of OS3 | Remarks
Voltage level upto 400 V and load upto 15 KW (Urban) | 30 | 128450 | 120415 | 8035
Voltage level upto 400 V and load upto 15 KW (Rural) | 45 | 222205 | 211127 | 11079 | 1- Non availability of material.
Voltage level upto 400 V and load upto 15 KW but not exceeding 70 KW | 53 | 9560 | 9089 | 471 | 2- Non verification of Test report
Voltage level upto 400 V and load above 70 KW but not exceeding 500 KW | 73 | 169 | 162 | 7
Voltage level upto 11 KV or 33 KV and load above 500 KW but not exceeding 5000 KW | 106 | 0 | 0 | 0 | 3- Civil Suit
Voltage level 166 KV and above for all load | 496 | 0 | 0 | 0

## Form6
Form-6
CONSUMER SERVICES AND SYSTEM PERFORMANCE ANNUAL REPORT 2020-21
Overall Standards - Nominal Voltages
Sheet 6
2020-21
Consumer Supply Voltage (OS4) | Maximum permitted voltage level deviations | Number of consumers who requested their power supply voltage level to be checked | Number of times where a remedial action followed a consumer request about his power supply voltage level check
220 KV (if applicable) | +/- 5% | - | -
132 KV | +/- 5% | - | -
66 KV | +/- 5% | - | -
33 KV | +/- 5% | - | -
11 KV | +/- 5% | 528 | 528
400/230 V Urban | +/- 5% | 1629 | 1629
400/230 V Rural | +/- 5% | 2151 | 2151
2019-20
Consumer Supply Voltage (OS4) | Maximum permitted voltage level deviations | Number of consumers who requested their power supply voltage level to be checked | Number of times where a remedial action followed a consumer request about his power supply voltage level check
220 KV (if applicable) | +/- 5% | - | -
132 KV | +/- 5% | - | -
66 KV | +/- 5% | - | -
33 KV | +/- 5% | - | -
11 KV | +/- 5% | 327 | 327
400/230 V Urban | +/- 5% | 2092 | 2092
400/230 V Rural | +/- 5% | 4204 | 4204

## Form7
Form-7
CONSUMER SERVICES AND SYSTEM PERFORMANCE ANNUAL REPORT 2020-21
Overall Standards - Frequency
Sheet 7
2020-21
Consumer Frequency | Maximum permitted frequency deviation | Total Number of consumers who requested their frequency level to be checked | Total Number of times where a remidial action followed a consumer request about his frequency level check
50 Hertz | + 1% | 131 | 131
2019-20
Consumer Frequency | Maximum permitted frequency deviation | Total Number of consumers who requested their frequency level to be checked | Total Number of times where a remidial action followed a consumer request about his frequency level check
50 Hertz | + 1% | - | -

## Form8
Form-8
CONSUMER SERVICES AND SYSTEM PERFORMANCE ANNUAL REPORT 2020-21
Overall Standards - Load Shedding
2020-21
Priority Group of Consumers | Number of Instances of actuation of load shedding (OS6) | Average duration of Load Shedding Period (Hours) | Maximum duration of load shedding period (Hours) | Number of consumers effected in each priority group | Load (MW) interrupted due to load shedding in each priority group
Consumers in Rural areas, and residential consumers in Urban areas | Urban - NIL Rural - 1 Times | Urban - 00:00 Hrs Rural - 00:40 Hrs | 01:00 Hrs | 0.3 Million | 56 MW (Appr)
Consumers other than Industrial in Urban areas | - | - | - | - | -
Agricultural consumers where there is dedicated supply | - | - | - | - | -
Industrial Consumers | Independent Industry NIL
Supply to Schools and Hospitals | Urban - NIL Rural - 1 Times | Urban - 00:00 Hrs Rural - 00:40 Hrs | 01:00 Hrs | 0.02 Million | 10 MW (Appr)
Defense / Strategic installation | Exempt from Load Shedding (92 Nos. Feeders) |  |  |  | NIL
a) Load Management Carried Out only on High Loss Feeders having AT&C Losses Category-III & Above in MEPCO.
2019-20
Priority Group of Consumers | Number of Instances of actuation of load shedding (OS6) | Average duration of Load Shedding Period (Hours) | Maximum duration of load shedding period (Hours) | Number of consumers effected in each priority group | Load (MW) interrupted due to load shedding in each priority group
Consumers in Rural areas, and residential consumers in Urban areas | Urban - NIL Rural - 2 Times | Urban - 00:00 Hrs Rural - 00:38 Hrs | 01:00 Hrs | 0.1 Million | 50 MW (Appr)
Consumers other than Industrial in Urban areas | - | - | - | - | -
Agricultural consumers where there is dedicated supply | - | - | - | - | -
Industrial Consumers | Independent Industry NIL
Supply to Schools and Hospitals | Urban - NIL Rural - 2 Times | Urban - 00:00 Hrs Rural - 00:38 Hrs | 01:00 Hrs | 0.01 Million | 08 MW (Appr)
Defense / Strategic installation | Exempt from Load Shedding (92 Nos. Feeders) |  |  |  | NIL

## Form9
Form-9
CONSUMER SERVICES AND SYSTEM PERFORMANCE ANNUAL REPORT 2020-21
Overall Standards - Safety
2020-21
Type of Incident | Number of Electrical Incidents | Average duration of Absence from Work | Longest duration of absesce from work
Electrical Incident resulting in death | 6 | - | -
Electrical incident resulting in injury to member of staff requiring hospital treatment or absence from work for five days or more | 8 | - | -
Electrical incident resulting in injury to member of staff requiring absence from work for 1-5 days | - | - | -
Electrical incident resulting in injury to member of staff not requiring absence from work | - | - | -
Electrical incident resulting in death or permanent serious injury/disability to member of public | 7 | - | -
Electrical incident injuring member of the public involving Distribution Company's plant or equipment | - | - | -
Electrical incident injuring member of the public not involving Distribution Company's plant or equipment | - | - | -
Safety reports received on toll free telephone number | - | - | -
2019-20
Type of Incident | Number of Electrical Incidents | Average duration of Absence from Work | Longest duration of absesce from work
Electrical Incident resulting in death | 10 | - | -
Electrical incident resulting in injury to member of staff requiring hospital treatment or absence from work for five days or more | 10 | - | -
Electrical incident resulting in injury to member of staff requiring absence from work for 1-5 days | - | - | -
Electrical incident resulting in injury to member of staff not requiring absence from work | - | - | -
Electrical incident resulting in death or permanent serious injury/disability to member of public | 3 | - | -
Electrical incident injuring member of the public involving Distribution Company's plant or equipment | - | - | -
Electrical incident injuring member of the public not involving Distribution Company's plant or equipment | - | - | -
Safety reports received on toll free telephone number | - | - | -

## Form 9 DA
Form-9
CONSUMER SERVICE AND SYSTEM PERFORMANCE ANNUAL REPORT
Overall Standards - Safety
SHEET 9 ( JULY-2020 TO JUNE-2021)
(FATAL ACCIDENT OF MEPCO EMPLOYEES)
Sr. # | i. Name / Design. Of Official ii. Date of accident | FIR Lodged (Yes / No) | Number of fatalities | Detail of accident | Extent of Injury | Name and contact detail of witness | Distribution Company's Inquiry Held or Not | i. Immediate Action Taken ii. Remidial actions proposed or taken | Name and occupation of persons involved | Punishment awarded to person involved.
1 | Fatal acciden of Muhammad Mubariz ALM (Authorized) and Non Fatal accident of Muhammad Pervaiz ALM of (OP) Karam Dad Qureshi Sub Division Kot Addu 12.07.2020 | NOT | 1 | On 12.07.2020 at about 12:05 hours a tragic accident occurred at Basti Mehry Wala Mouza Saidan Wali Tehsil & District Muzaffar Garh in the area of MEPCO (OP) Sub Division Karam Dad Qureshi under Division / Circle Muzaffar Garh in which Muhammad Mubariz S/O Shams-ul-Haq ALM (Authorized) met with fatality and Muhammad Pervaiz S/O Ghulam Shabbir ALM injured with heavy spark on his face and shifted for treatment at D.H.Q Hospital Muzafar Garh. As per initial investigation, it was found that on 29.06.2020 at 03:27 & 03:50 PM, SE (OP) MEPCO Circle Muzaffar Garh sent a whatsapp message to XEN (OP) MEPCO Division Muzaffar Garh and SDO (OP) Sub Division Karam Dad Qureshi for the removal of hazardous point of broken HT pole at Basti Mehry Wala Mouza Saidan Wali. In compliance of which SDO sent a message to XEN (OP) MEPCO Division Muzaffar Garh on Saturday 11.07.2020 for emergent PTW of 11-KV Faiz Imam feeder required on Sunday 12.07.2020 for replacement of 11-KV broken pole. On Sunday 12.07.2020 at 07:10 hours Mr. Abdul Ghaffar LS-II obtained PTW No. 232692 on same feeder by creating break down on feeder and got it cancelled at 08:20 hours after cutting the HT jumpers of line before broken HT PCC pole. The staff consisting upon Mr. Sajid Raza LS-II, three linemen named Ghulam Rasool LM-I (Concerned), Nawazish Ali LM-I, Koray Khan LM-I, Muhammad Mubariz ALM (Auhotirzed), Muhammad Pervaiz ALM and Muhammad Tahir ALM were already present at site. They started the shifting of 11-KV conductor from broken pole to new PCC HT pole and completed stringing of one phase with the help of Coughing Hoist and Wire Grip, but while sagging the 2nd wire, all of sudden, the conductor slipped through the rope with tension and touched with parallel running 132-KV line which was about 12 to 15 feet away from HT PCC pole. Resultantly a blast occurred and Muhammad Mubariz ALM (Authorized) received severe electric shock whereas other co-worker Muhammad Pervaiz ALM got big spark on his face and became unconscious on the pole. Both victims were brought down by Ghulam Rasool LM-I and were shifted to D.H.Q Hospital Muzaffar Garh by Rescue (1122) where one Muhammad Mubariz was declared dead and other victim Muhammad Pervaiz was got admitted after First Aid in emergency and now he is on duty. | Muhammad Mubariz ALM (Authorized) received severe electric shock and expired whereas other co-worker Muhammad Pervaiz ALM got big spark on his face and he became injured | 1- Raye Fida Hussain Public Man R/O Basti Mehray Walal Mouza Saidan Wali | Finalized | 1- Mr. Muneer Hussain Razi LS-I / Acting SDO suspended vide SE (OP) MEPCO Circle Vehari O/O No. 527/18433-40 dated: 04.09.2019 2- Mr. Muhammad Ashraf LS-II suspended vide SE (OP) MEPCO Circle Vehari O/O No. 268/3615-24 dated: 19.08.2019 3- Mr. Muhammad Ishfaq ALM suspended vide XEN (OP) MEPCO Division Burewala O/O No. 377/16913-18 dated: 19.08.2019 | 1- Mr. Muhammad Umair Qasim XEN Under Process 2- Mr. Shahid Nawaz SDO Under Process 3- Mr. Sajid Raza LS-II 4- Mr. Abdul Ghaffar LS-II 5- Mr. Ghulam Rasool LM-I 6- Koray Khan LM-I 7- Nawazish Ali LM-I 8- Tahir Razzaq ALM 9- Muhammad Pervaiz ALM | 1- Mr. Sajid Raza LS-II Two step down for one year vide O/O No. 204/1747-53 dated: 20.11.2020 2- Mr. Abdul Ghaffar LS-II Two step down for one year vide O/O No. 203/1741-46 dated: 20.11.2020 3- Mr. Ghulam Rasool LM-I Demoted from LM-I to LM-II for the period of two year vide O/O No. 685/5884-90 dated: 30.09.2020 4- Koray Khan LM-I Reduction to lower two stage down in his time scale for the period of two year vide O/O No. 687/5898-5904 dated: 30.09.2020 5- Nawazish Ali LM-I Demoted from LM-I to LM-II for the period of one yearvide O/O No. 686/5891-97 dated: 30.09.2020 6- Tahir Razzaq ALM Reduction of one step down in his time scale for one year vide O/O No. 744/6442-48 dated: 28.10.2020 7- Muhammad Pervaiz ALM Withdrawn vide O/O No. 688/5905-07 dated: 30.09.2020
2 | Muhammad Usman Khurram ALM of (OP) Sub Division Maroot 17.07.2020 | NOT | 1 | Victim was climbing up the HT pole to assist LM for the replacement of broken Wooden X Arm. He slipped from ladder and fell on ground and received inner body injuries. He was shifted to Bahawal Victoria Hospital Bahawal Pur but he expired after 6 hours of accident. | He slipped from ladder and fell on ground and received inner body injuries and he was expired after 6 hours of accident. | 1- Farhat Abbass LM-II MEPCO (OP) Sub Division Maroot 2- Waris Ali ALM MEPCO (OP) Sub Division Maroot | Finalized | NIL | 1- Mr. Zulfiqar Ali SDO 2- Mr. Zeeshan-ul-Haq LS-II 3- Mr. Tahir Javed LM-I | 1- Mr. Abdul Wahid (DDT) Bahawal Nagar Warning Letter No. 3844 dated: 23.11.2020 issued 2- Mr. Zulfiqar Ali SDO Warning Letter No. 3845-46 dated: 23.11.2020 issued 3- Mr. Zeeshan-ul-Haq LS-II LOE No. 3847 dated: 23.11.2020 issued 4- Mr. Tahir Javed LM-I LOE No. 56 dated: 18.11.2020 issued
3 | Wazir Ahmed LM-I of (OP) Qadir Abad Sub Division Sahiwal 08.08.2020 | NOT | 1 | On 08.08.2020 at about 08:30 AM, Mr. Wazir Ahmed LM-I of MEPCO (OP) Sub Division Qadir Abad, Division 1st Sahiwal under MEPCO (OP) Circle Sahiwal, met with fatal accident while climbing down, he slipped from structure pole after attending electricity failure complaint of consumer in the name of Mr. Umer S/O Anayat bearing A/C No. 17-15516-0679501 R/O Chak No. 62/15-L Qadir Ababd, his head hit on a brick and bleeding started from his nose and mouth. He was shifted to D.H.Q Hospital Sahiwal where duty officer doctor, after performing ECG declared him expired. | He slipped from structure pole, his head hit on a brick and bleeding started from his noise and mouth | 1- Rana Shahbaz S/O Muhammad Aslam Public Man R/O Chak No. 62/5-L Sahiwal 2- Umer S/O Anayat-Ullah Public Man R/O Chak No. 62/5-L Sahiwal | Finalized | NIL | 1- Mr. Arslan Ahmed SDO 2- Mr. Shafqat Hussain LS-II | Under Process
4 | Muhammad Abu Zar Crane Operator of (OP) Division D.G.Khan 16.08.2020 | NOT | 1 | The victim was removing a 50-KVA Transformer without PTW by taking the support of jack pillar of crane when all of a sudden the boom of crane touched with the 11-KV jumper upper side of D-Fitting. He received electric shock and expired. | He received electric shick and expired | 1- Muhammad Asif Contractor Labourer and working as ALM in MEPCO (OP) Queeta Road Sub Division D.G.Khan | Finalized | 1- Mr. Muhammad Asif LS-I suspended vide SE (OP) MEPCO Circle D.G.Khan O/O No. 51-T/2803-07 dated: 17.08.2020 2- Mr. Muhammad Asgher Bloch LM-I suspended vide XEN (OP) MEPCO Division D.G.Khan O/O No. 340/1816-23 dated: 17.08.2020 | 1- Mr. Muhammad Imran Mehmood SE 2- Mr. Mumtaz Ahmed Solangi XEN 3- Mr. Faiz Rasoo SDO 4- Mr. Muhammad Asif LS-I | Under Process
5 | Muhammad Sarfraz ALM of (OP) Rural Sub Division Lodhran 24.10.2020 | NO | 1 | Mr. Muhammad Sarfraz S/O Haq Nawaz, ALM of MEPCO (OP) Rural Sub Division Lodhran, Division Lodhran under MEPCO (OP) Circle Bahawal Pur met with fatal accident on 24.10.2020 at about 13:00 hours while attending the complaint of supply failure of Tube Well connections bearing A/C No. 29-15422-0030800 in the name of Rana Rab Nawaz Khan and A/C No. 29-15422-0074800 in the name of Rana Naseem Khan due to broken LT conductors from 50-KVA Transformer Sub Station at Mouza Ram Kali near 05 Mrala Scheme Lodhran. The victim was working without proper PPE, except only with safety belt by cut off the main D-Fuses of branch line of 11-KV Shaheedan feeder emanating from 132-KV Grid Station Lodhran. Two duty linemen of said feeder were also with him but one was sitting beneath the main D-Set after cutting off the fuses whereas 2nd was present on the ground at work place of 50-KVA Transformer Sub Station who deputed the ALM to climb up the pole to set right the broken LT conductor. The victim after fastened the safety belt strap with the structure pole, as started to work, his hand touched with a single LT phase conductor wire which was binded on same pole but was energized from another 200-KVA Transformer of Basti 05 Marla Scheme. He received electric shock and expired which was later on confirmed by duty doctor of D.H.Q Hospital Lodhran. | He received electric shock from single phase LT conductor | 1- Usman Ghani S/O Allah Ditta Public Man R/O Basti 05-Marla Scheme Lodhran | Finalized | 1- Mr. Iqbal Hussain LM-I suspended vide XEN (OP) MEPCO Division Lodhran O/O No. 134/ 2702-08 dated: 24.10.2020 2- Mr. Muhammad Shareef LM-I suspended vide XEN (OP) MEPCO Division Lodhran O/O No. 133/2695-2701 dated: 24.10.2020 | 1- Mr. Muhammad Akram Javed Addl: XEN / SDO 2- Mr. Hafiz Umar LS-II 3- Mr. Iqbal Hussain LM-I 4- Mr. Muhammad Shareef LM-I | Under Process
6 | Muhammad Hanif LM-II of (OP) Rahim Abad Sub Division Sadiq Abad 23.12.2020 | NO | 1 | On 23.12.2020 at about 13:00 hours, Muhammad Hanif S/O Muhammad Mosa LM-II of MEPCO (OP) Sub Division Rahim Abad, Division Sadiq Abad under MEPCO (OP) Circle Rahim Yar Khan met with fatal accident while working on 11-KV Nawaz Abad feeder, emanating from 132-KV Grid Station Sadiq Abad. The deceased was working under PTW for connecting the 11-KV jumpers to energized the 3 span HT line extended for LT Proposal near Basti Bambay Shaheed Ahmed Pur Lamha Sadiq Abad but due to touching of one phase of another energized 11-KV Kandair feeder at a crossing point located near Dera Ch.: Arshad Ahmed Pur Lamha victim received electric shock and expired at spot. His body was brought down from pole and staff of Rescue 1122 shifted at R.H.C Ahmed Pur Lamha where duty doctor also declared died then dead body was shifted to his home Hashmi Colony near Ahmed Pur Lamha Sadiq Abad. | He received 11-KV electric shock and multiple wounds of burning on his body particularly the area of left under arm became maximum damaged | 1- Zulfiqar Ali S/O Muhammad Shoukat Ali Public Man R/O Hashmi Colony Ahmed Pur Lamha Sadiq Abad 0307-0032725 | Finalized | 1- Mr. Nadeem Jamal LS-II suspended vide SE (OP) MEPCO Circle Rahim Yar Khan O/O No. 382/ 3629-33 dated: 24.12.2020 | 1- Mr. Asim Rasheed XEN 2- Mr. Allah Din the then Acting SDO now LS-I 3- Mr. Abdul Jabbar SDO 4- Mr. Nadeem amal LS-II | Under Process
Form-9
CONSUMER SERVICE AND SYSTEM PERFORMANCE ANNUAL REPORT
Overall Standards - Safety
Sheet 9 ( JULY-2020 TO JUNE-2021)
(NON FATAL ACCIDENT OF MEPCO EMPLOYEES)
Sr. # | i. Name / Design. Of Official ii. Date of accident | FIR Lodged (Yes / No) | Number of fatalities | Detail of accident | Extent of Injury | Name and contact detail of witness | Distribution Company's Inquiry Held or Not | i. Immediate Action Taken ii. Remidial actions proposed or taken | Name and occupation of persons involved | Punishment awarded to person involved.
1 | Nazim Hussain Acting LM of (OP) Fazil Pur Sub Division Rajan Pur 13.08.2020 | NO | NIL | On 13.08.2020 at about 15:30 hours, Nazim Hussain ALM (acting LM) S/O Raheem Bakhsh of MEPCO (OP) Sub Division Fazil Pur, Division (OP) Rajan Pur under MEPCO (OP) Circle Dera Ghazi Khan met with a non fatal accident while removing a direct kunda from Single Phase LT line near 50-KVA Transformer Sub Station of 11-KV Sahan Wala feeder at Basti Shahmeer Fazil Pur. The victim was standing on the ground and was pulling the Single Phase PVC cable with bare hands, i.e. gripping structure pole with his left hand with foot on structure pole when PVC cable jumped and touched with 11-KV Transformer jumper due to which blast occurred and Nazim Hussain received electric shock and fell on the ground unconsciously. Electric current affected his both hands, left shoulder, under arm and crossed from right leg. Mr. Ghulam Yaseen LM-I was also with him at site who along with local people shifted him to hospital where First Aid was provided and after some time he was referred to District Hospital Rajan Pur for further treatment. Now he is still under treatment at his home. | Electric current affected his both hands, left shoulder, under arm and crossed from right leg | 1- Mr. Ghulam Yaseen LM-I MEPCO (OP) Sub Division Fazil Pur | Finalized | NIL | 1- Mr. Zakirt Hussain Dhani XEN 2- Mr. Muhammad Yasir SDO 3- Mr. Ghulam Asghar LM-I (Acting LS) 4- Mr. Ghulam Yaseen LM-I 5- Nazim Hussain ALM (Acting LM) | Under Process
2 | Bahisr Ahmed LM-I of (OP) Sub Division Sardar Pur Jhandir Mailsi 21.01.2021 | NO | NIL | On 21.01.2021 at about 14:35 hours, Bashir Ahmed LM-I S/O Wahid Bakhsh, MEPCO (OP) Sub Division Sardar Pur Jhandir, Division (OP) Mailsi under MEPCO (OP) Circle Vehari met with non fatal accident while working on 100-KVA Distribution Transformer Sub Station at Basti Rasool Pur Mouza Rohla Tehsil Mailsi District Vehari. The official along with Zaki-ul-Hasnain ALM was attending a complaint to set right the Red Phase HT jumper near D-Fuse fitting without PTW just to get the tripping on 11-KV Safeer Nagar feeder manually from shift duty Incharge 132-KV Grid Station MEPCO Mailsi but during such working through illegal way, the feeder was switched on due to lack of communication and Bashir Ahmed LM-I faced electrocution, hanged on structure pole unconsciously with the support of safety belt and Wooden X-Arm of D-Set fitting. Upon his roaring, the people of area gathered there and informed the concerned staff as well as Rescue 1122 as Zaki-ul-Hasnain ALM who became puzzle / not able to rescue him on pole without confirming the closure of feeder supply from Grid Station so he remained hanged for 20 to 25 minutes and after confirmation the supply off, victim was brought down. He received multiple wounds of electric burns on various parts of his body so was shifted to Tehsil Head Quarter Hospital Mailsi where he was provided First Aid and other medical treatment during which he became in conscious but after due consultation with duty officer doctor and keeping in view his severe external body condition, XEN (OP) Division Mailsi and SDO (OP) Sub Division Sardar Pur Jhandir got him referred to shift Nishter Hospital Multan on same day for better treatment. | He received multiple wounds of electric burns on various parts of his body | 1- Choudry Muhammad Arif S/O Jan Muhammad R/O Basti Rasool Pur | Finalized | 1- Mr. Muhammad Mushtaq LS-II suspended vide Addl: Chief Engineer MEPCO (OP) Circle Vehari O/O No. 07/179-85 dated: 22.01.2021 2- Mr. Zaki-ul-Hasnain ALM suspended vide Addl: Chief Engineer MEPCO (OP) Circle Vehari O/O No. 08/186-92 dated: 22.01.2021 | 1- Mr. Ameer Abbas SDO 2- Mr. Qaswar Abbas SSO-I 3- Mr. Bashir AHmed LM-I 4- Mr. Zaki-ul-Hasnain ALM | Under Process
3 | Muneer Ahmed Fitter-I of 132-KV Grid Station Shadan Lund 28.04.2021 | NO | NIL | On 08.04.2021, during six monthly maintenance of T-1 20/26 MVA Transformer with allied equipment and panels, back side panel plate of 11-KV Shadan Lund and 11-KV Kareem Wala feeder were interchanged mistakenly. On 28.04.2021 at 23:35 hours, 11-KV outgoing Shadan Lund feeder tripped off on three phase fault due to panel side cable burst and said feeder declared under breakdown. Grid incharge informed AET SS&T Sub Division Shadan Lund who directed Muneer Ahmed Fitter-I to reach the Grid Station. (Concerned LS Khalid Mehmood of (OP) Sub Division Shadan Lund obtained PTW on 11-KV Shadan Lund feeder at 01:20 hours and PTWs on 11-KV Kareem Wala and 11-KV Atomic-2 feeder for safety purpose. Line staff opened cable connection of 11-KV SHadan Lund feeder from terminal pole and Grid Incharge along with Grid Staff opened panel back side lower plate of Kareem Wala feeder panel wrongly because back side panel plate of 11-KV Shadan Lund and 11-KV Kareem Wala feeder were mistakenly interchanged. On Direction of AET (SS&T) Sub Division Shadan Lund, Muneer Ahmed Fitter-I reached 132-KV Grid Station and found cable connections open from terminal poles of Shadan Lund feeder and both trolleys of 11-KV Shadan Lund and Kareem wala feeder racked out at 01:15 hours on 29.04.2021 and backside lower plate of Kareem Wala feeder because on plates Shadan Lund was written removed. He without counting panels from front and backside / verification of panels removed backside cables and started testing with Meggar but result was not found OK. He removed 1st two cables earthing wires, meanwhile Mr. Muhammad Moeen SSA shift incharge racked in the trolley of 11-KV Kareem Wala feeder on cancellation of PTW without informing to Muneer Ahmed Fitter-I and Fitter-I while removing 3rd cable earthing wire, came in induction zone of backside of energized panel, a big flash occurred. Face and both hands of Fitter-I was severely affected. | Face and both hands of Fitter-I was severely affected. | 1- Waseem Delawar ASSA (SS&T) Maintenance Sub Division D.G.Khan | Finalized | 1- Mr. Ghulam Yasin SSO-II suspended vide Addl: Chief Engineer GSO Multan O/O No. 346/O-2/5216-20 dated: 04.05.2021 2- Mr. Munir Ahmed Fitter-I suspended vide Addl: Chief Engineer GSO Multan O/O No. 347/O-2/5221-25 dated: 04.05.2021 | 1- Mr. Zahid Iqbal Foreman 2- Mr. Ghulam Yasin SSO-II 3- Mr. Muneer Ahmed Fitter-I 4- Mr. Sajjad Naveed AET 5- Ubaid-Ullah Khosa Additional XEN | Under Process
4 | Akhter Hussain LM-I of (OP) Industrial Estate Sub Division Multan 30.04.2021 | NO | NIL | The victim official was working on HT Pole for shifting the load of a feeder to other one under PTWs when he received electric shock during ser righting the HT jumper, met with non fatal accident and now is under treatment | Burntage wounds on both thigs of leg | 1- Muhammad Asim ALM MEPCO (OP) Industrial Estate Sub Division Multan | HELD | 1- Mr. Akhter Hussain LM-I suspended vide XEN (OP) MEPCO Cantt Division Multan O/O No. 2474/15071-74 dated: 04.05.2021 | Under Process | Under Process
5 | Liaqat Ali LM-II of (OP) Sub Division Harappa 26.05.2021 | NO | NIL | The victim was set righting the HT jumper of Transformer without PTW rather getting the feeder supply tripped for some time on phone when he received electric shock, fell on the ground and met with non fatal accident. | Burntage wounds on his hand | NIL | HELD | 1- Mr. Ghulam Mustafa LS-I suspended vide XEN (OP) MEPCO 2nd Division Sahiwal O/O No. 351/3432-35 dated: 25.05.2021 2- Mr. Liaqat Ali LM-II suspended vide XEN (OP) MEPCO 2nd Division Sahiwal O/O No. 352/3428-31 dated: 26.05.2021 | Under Process | Under Process
6 | Sajjad Hussain Acting LM of (OP) Sub Division Shadan Lund 12.06.2021 | NO | NIL | On 12.06.2021 at about 11:25 AM, Mr. Sajjad Hussain S/O Muhammad Ramzan (Acting LM) of MEPCO (OP) Sub Division Shadan Lund, met with non fatal accident while removing spare Insulators fixed on Wooden Cross Arm installed on HT structure pole without checking / providing earthing on 11-KV line as he reached near 11-KV line, his left arm and face came in induction zone, he received flash on his face and left arm because 11-KV Shadan Lund feeder was just switched ON by Grid Staff on cancellation of PTW No. 2855 by Mr. Khalid Mehmood LS-II. | he received flash on his face and left arm | 1- Abdul Majeed ALM MEPCO (OP) Sub Division Shadan Lund | Finalized | 1- Mr. Abdul Majeed LM-II suspended vide XNE (OP) MEPCO Division Tounsa O/O No. 273 dated: 13.06.2021 2- Khalid Mehmood LS-II suspended vide SE (OP) MEPCO Circle D.G.Khan O/O No. | 1- Mr. Muhammad Aslam LS-I 2- Mr. Khalid Mehmood LS-II 3- Mr. Abdul Majeed LM-II 4- Mr. Sajjad Hussain Acting LM | Under Process
7 | Nabi Bakhsh LM-II of (OP) Sub Division Khanqah Sharif 16.06.2021 | NO | NIL | On 16.06.2021, at about 13:30 hours Mr. Nabi Bakhsh S/O Allah Dewaya LM-II MEPCO (OP) Khanqah Sharif, Division (OP) Model Town under (OP) MEPCO Circle Bahawal Pur met with non fatal accident while connecting the 11-KV jumper upper from D-fitting of 25-KVA independent Tube well Transformer without PTW rather by cut off the main branch line fuses. | he screamed from HT electric shock on his hand | 1- Muhammad Imran ALM MEPCO (OP) Sub Division Khanqah Sharif | HELD | 1- Mr. Khadim Hussain LS-II suspended vide XNE (OP) MEPCO Model Town DIvision O/O No. 113/565-71 dated: 16.06.2021 | Under Process | Under Process
Form-9
CONSUMER SERVICE AND SYSTEM PERFORMANCE ANNUAL REPORT
Overall Standards - Safety
Sheet 9 ( JULY-2020 TO JUNE-2021)
(FATAL/NON FATAL ACCIDENT OF GENERAL PUBLIC)
Sr. # | i. Name / Design. Of Official ii. Date of accident | FIR Lodged (Yes / No) | Number of fatalities | Detail of accident | Extent of Injury | Name and contact detail of witness | Distribution Company's Inquiry Held or Not | i. Immediate Action Taken ii. Remidial actions proposed or taken | Name and occupation of persons involved | Punishment awarded to person involved.
1 | Saweera Bibi Public Girl MEPCO (OP) Sub Division Sarai Sadhu 01.09.2020 | NIL | 1 | Mst: Saweera Bibi age about 12 Years met with fatal accident due to electocution in Basti Saleem Abad near Adda Choppar Hatta in the area of MEPCO (OP) Sub Division Sarai Sadhu. | She received electric shock and died | NIL | Finalized | NIL | 1- Mr. Nasrullah Khan Nasir XEN 2- Mr. Mubashir Jamal Saleemi SDO 3- Mr. Zubari Ahmed LS-II 4- Mr. Bashir Ahmed LM-I 5- Akhter Hussain ALM | Under Process
2 | Muhammad Yasir Public Boy MEPCO (OP) Sub Division Khair Pur Sadat 24.11.2020 | NO | 1 | A news about electrocution of a public boy was published dated 26.11.2020 in news paper “Daily Khabrain” and came in the notice of Chief Executive Officer MEPCO Multan on 10.12.2020 upon which Safety Directorate MEPCO was directed to conduct immediate enquiry. On 24.11.2020 at about 12:30 hrs, a public boy named Muhammad Yasir S/O Muhammad Iqbal having age near to 16 Years, resident of Basti Peero Shahi Mouza Khanani Tehsil Ali Pur District Muzaffar Garh met with fatal accident by electrocution due to touching with the bare joint of PVC cables while to set right the cable of home supply near to his Basti in the area of MEPCO (OP) Sub Division Khair Pur Sadat Division Ali Pur under MEPCO (OP) Circle Muzaffar Garh | electrocution due to touching with the bare joint of PVC cables | 1- Muhammad Javed S/O Hazoor Bakhsh R/O Mouza Khanani Basti Peroo Shahi Tehsil Alli Pur | Finalized | NIL | 1- Mr. Muhammad Yaqoon XEN 2- Mr. Muhammad Imran SDO 3- Mr. Ghulam Asghar LM-I (Acting LS) 4- Mr. Ghulam Yaseen LM-I 5- Nazim Hussain ALM (Acting LM) | Under Process
3 | Muhammad Zeeshan Public Man MEPCO (OP) Sub Division Jatoi 30.11.2020 | NO | 1 | Mr. Muhammad Zeeshan S/O Abdul Sittar (Public Man) met with fatal accident on 30.11.2020 at about 19:30 hours to 20:00 hours due to touching with fallen HT live conductor of 11-KV Sithari feeder at Basti Jam Mouza Khalti Jatoi. The HT conductor of 11-KV Sithari feeder emanating from 132-KV Grid Station Jatoi before in the evening of 30.11.2020 due to some fault and was lying slightly uplifted from ground at Basti Jam which also blocked the passage of Basti and people of area were crossing it from the side of field when in the darkness victim Muhammad Zeeshan was coming on motorcycle without headlight and front wheel of bike struck with the live conductor due to which sparks occurred and he received severe electric shock and expired at spot. | He received severe electric shock and expired at spot | 1- Muhammad Tayyab R/O Basti Mano Wala Tehsil Jatoi District Muzaffar Garh 2- Usman Ghani S/O Haji Abdul Ghani R/O Basti Mano Wala Tehsil Jatoi District Muzaffar Garhh | Finalized | NIL | 1- Mr. Allah Bachaya SDO 2- Mr. Abdul Sattar LS-I 3- Mr. Shahid Iqbal LS-II 4- Mr. Ghulam Shabbir LM-II 5- Mr. Iqbal Shah LM-II 6- Yaqoob Ahmed XEN | Under Process
4 | Shabbir Ahmed Ex-ALM Public Man MEPCO (OP) Sub Division Manzoor Abad Multan 02.04.2021 | NO | 1 | On 02.04.2021 at about 08:45 hours, Mr. Shabbir Ahmed S/O Muhammad Bakhsh, Ex-Employee (ALM) of MEPCO (OP) Sub Division / Division Shah Rukne-Alam under MEPCO (OP) Circle Multan met with fatal accident when he climbed up the PCC LT pole and wrapped the PVC around the pole for making the jumper of single phase new connection meter for connecting with the 3 phase LT line of 11-KV new Vehari Road feeder at Kho Tariyan Wala Bhaini Shakan Wali Mouza Kot Rab Nawaz Tehsil / District Multan. The dead end LT PCC pole was deteriorated from ground level with rusted two iron bars could not bear the load of victim Shabbir Ahmed and bamboo ladder as the ladder was fixed with the pole by using the roof of nearby house of Muhammad Akmal S/O Muhammad Riaz, also against the direction of Stay Wire, at 90’ angle with the result he fell down on the ground along with PCC pole and ladder. The inner side of chin hit with the edge of pole, his one leg fractured and injured badly. The applicant customer Muhammad Shahid S/O Muhammad Sharif was present there at site with his real brother Muhammad Junaid. They informed to Rescue (1122) as well as police and isolated the victim from pole by untying the safety belt but he had become unconscious as he fell down. They with the help of other people laid the victim on a cart and tried to bring him in conscious but he had passed away which was confirmed by Rescue (1122) as they arrived in almost 15 minutes. In the meantime someone from gathered people informed MEPCO Employees and his home whereas the police of concerned area also reached at spot and shifted the deceased first to Nishter Hospital Multan then to his home. | The inner side of chin hit with the edge of pole, his one leg fractured and injured badly. | NIL | Finalized | 1- Mr. Hassan Nisar Gardezi LS-II suspended vide SE (OP) MEPCO Circle Multan O/O No. 259/ 2936-46 dated: 02.04.2021 2- Mr. Muhammad Hanif ALM suspended vide XNE (OP) MEPCO Division Shah Rukne Alam Multan O/O No. 305/5720-26 dated: 02.04.2021 | 1- Mr. Hassan Nisar Gardezi LS-I 2- Mr. Muhammad Hanif ALM 3- Mr. Ghulam Mustafa Mujahid the then SDO 4- Mr. Azam Ali Qureshi SDO 5- Mr. Usman Majeed LS-I 6- Mr. Arshad Sindhu LM-I | Under Process
5 | Saeed Public Man MEPCO (OP) Powe House Sub Division Pakpattan 12.05.2021 | NO | 1 | Unauthorized private person climbed up the 11-KV poles to disconnect the HT jumper of faulty branch and received electric shock from feed back back supply of damaged independent Transformer energized from genrator supply due to fault of changeover switch. |  | NIL | HELD | NIL | Under Process | Under Process
6 | Muhammad Shahbaz Public Man MEPCO (OP) Gulshan Iqba Sub Division Rahim Yar Khan 22.05.2021 | NO | 1 | On 22.05.2021 at about 23:30 hrs a public man (Private Electrician) namely Muhammad Shahbaz S/O Naqsh Muhammad, resident of Tarinda Saway Khan, Tehsil / District Rahim Yar Khan met with fatal accident when he was working on HT structure pole of 200-KVA Transformer Sub Station at Chak No. 99/P Rahim Yar Khan without PTW by cut off the main line branch fuses on 11-KV feeder Rehman Pur, emanating from 132-KV Grid Station Rahim Yar Khan-II in the area of MEPCO (OP) Sub Division Gulshan Iqbal Division / Circle Rahim Yar Khan. The deceased hanged with the support of safety belt and expired at spot as he received severe HT electric shock while opening the 11-KV jumper of Basti Chak No. 99/P where an 11-KV PCC pole bent down due to heavy windstorm. The victim could not be rescued timely due to rain and storm, he remained in hanging position for more than one and half hour and then brought down jointly by Rescue 1122 and Muhammad Irfan LM-II of Gulshan Iqbal Sub Division but few parts of his body found the signs of burnt wounds. Rescue 1122 shifted the dead body of Muhammad Shahbaz Private Electrician to his home. | He received severe HT electric shock and died at the spot | 1- Muhammad Shahid Iqbal R/O Chak No. 99/P Tehsil & District Rahim Yar Khan | Finalized | 1- Mr. Tahir Mustafa LM-II / Acting LS suspended vide XEN (OP) MEPCO Division Rahim Yar Khan O/O No. 46/8816-22 dated: 23.05.2021 2- Mr. Muhammad Shahid LM-I / Acting LS suspended vide XEN (OP) MEPCO Division Rahim Yar Khan O/O No. 47/8805-15 dated: 23.05.2021 3- Mr. Muhammad Irfan LM-II suspended vide XEN (OP) MEPCO Division Rahim Yar Khan O/O No. 45/8800-8804 dated: 23.05.2021 | 1- Mr. Muhammad Shahid LM-I (Acting LS) 2- Mr. Tahir Mustafa LM-II (Acting LS) 3- Mr. Muhammad Irfan LM-II 4- Mr. Muhammad Faisal SDO 5- Shahzad Habib Gill XEN | Under Process
7 | Attaullah Public Man MEPCO (OP) Gulshan Abad Sub Division Kot Chutta 29.05.2021 | NO | 1 | On 28.05.2021 heavy windstorm disturbed the power supply of MEPCO (OP) Sub Division Jampur and Gulshanabad. All distribution feeders of both Sub Divisions went under break down at 04:30 PM approx. After stoppage of rain and wind PTWs were obtained and supply was restored respectively after disconnection of faulty area. PTW No.3084 was also obtained on 11 KV Bukhara feeder at 19:20 PM by Allah Dewaya LS-II feeder Incharge. 11 KV Bukhara Feeder has 109 KM length of HT with a Number of branches and sub branches. The supply of Bukhara feeder was restored at 21:30 PM after disconnecting different branches and supply restored up to same Nala D-Set at 15 Amp. Next day on 29.05.2021 early in the morning Muhammad Ali Haideri LM-II started patrolling on 11 KV Bukhra feeder on instructions of Allah Dewaya LS feeder Incharge. He took Mr. Qaiser Abbas LM-II with him and deputed him on same Nala D-Set as supply was running upto that point. He took Mr. Attaullah (Private Electrician) with him and started patrolling of feeder and disconnected the branches. At nearly 10:00 AM he disconnected the Dead jumpers of Qamber Shah branch. Mr. Attullah was also there. After disconnection of dead jumpers of Qamber Shah branch Muhammad Ali deputed Attaullah for patrolling of Qamber Shah branch and he himself departed for patrolling of Salam Pur branch. Mr. Attaullah reached Nala Slamabad at nearly 10:30 AM from where a T-off towards east eminates from Qamber Shah branch. At 10:36 AM he had discussion with Muhammad Ali Haideri LM (call record shows 25 sec from Attaullah to Muhammad Ali). Then he climbed up the pole without testing the 11 KV line and aquring any safety measure. As eye witnesses at site which were also relative to him stated he had sufficient items of T&P / PPE along with Beeper but he was so confident about the line that he climbed up pole blindly and immediately fell downs due to electric shock because Mr. Qaisar Abbas LM-II connected D-Links of Same Nala D-Set on the direction of Mr. Muhammad Ali LM-II which caused back energization of that branch. | He received severe HT electric shock and died at the spot | NIL | Finalized | 1- Mr. Jam Allah Dewaya LS-I suspended vide SE (OP) MEPCO Circle D.G.Khan O/O No. 798/6661-68 dated: 29.05.2021 | 1- Mr. Abdul Khaliq Jarwar SDO 2- Mr. Allah Dewaya LS-II 3- Mr. Muhammad Ali Haideri LM-II 4- Mr. Qaisar Abbas LM-II | Under Process

## Form10
CONSUMER SERVICES AND SYSTEM PERFORMANCE FOR 2020-21
Consumer Formal Complaints Report
Sheet 10
2020-21
Nature of Complaint | Received in Person | Received by Telephone | Received Electronically | Received in writing | Average Time in Hrs to resolve a complaint | Longest Time in Hrs to resove a Complaint
Price of Electricity | 5760 | 7637 | 1664 | 2290 | 1 to 2 | 3 to 4
Reliability of Supply | 13890 | 81147 | 26564 | 1440 | 1 to 2 | 3 to 4
Planned Interruptions | 1721 | 3383 | 2114 | 1798 | 1:30 to 2:30 | 6 to 7
Supply Voltage Level | 3177 | 15433 | 8030 | 508 | 1:30 to 2:30 | 4 to 5
New Connection | 4051 | 7346 | 3627 | 1107 | 12 to 24 | 24 to 48
Safety | 246 | 338 | 574 | 157 | 1/2 to 1 | 1
Other | 11142 | 11027 | 7655 | 3045 | 0 | 0
2019-20
Nature of Complaint | Received in Person | Received by Telephone | Received Electronically | Received in writing | Average Time in Hrs to resolve a complaint | Longest Time in Hrs to resolve a complaint
Price of Electricity | 1702 | 1086 | 923 | 1563 | 1 to 2 | 3 to 4
Reliability of Supply | 10968 | 90509 | 13114 | 1578 | 1 to 2 | 3 to 4
Planned Interruptions | 1585 | 2454 | 2288 | 1272 | 1:30 to 2:30 | 6 to 7
Supply Voltage Level | 5076 | 14156 | 9646 | 739 | 1:30 to 2:30 | 4 to 5
New Connection | 1607 | 681 | 974 | 1292 | 12 to 24 | 24 to 48
Safety | 400 | 597 | 518 | 352 | 1/2 to 1 | 1
Other | 20384 | 18921 | 9146 | 4562 | 0 | 0

## Form11
Form-11
CONSUMER SERVICES AND SYSTEM PERFORMANCE FOR 2020-21
System Performance
Sheet 11
2020-21
System Voltage | Total Length of Distribution System in Service (KM) | Total Number of Distribution System fault | Faults/KM of distribution system
220 KV (if applicable) | - | - | -
132 KV | 26.2 | 94 | 3.587
66 KV | - | - | -
33 KV | - | - | -
11 KV | 1731.04 | 9476 | 5.474
400/230 V | 50333 | 332133 | 6.598
2019-20
System Voltage | Total Length of Distribution System in Service (KM) | Total Number of Distribution System fault | Faults/KM of distribution system
220 KV (if applicable) | - | - | -
132 KV | 7.6 | - | -
66 KV | - | - | -
33 KV | - | - | -
11 KV | 1255.752 | 8633 | 6.87
400/230 V | 50110 | 377630 | 7.53

## Billing
BILLING AND COLLECTION (Computed W/O Subsidy)
F.Y. 2020-21
Rs. in Million
Month | BILLING |  |  | COLLECTION |  |  | %AGE COLLECTION
| Private | Govt | Total | Private | Govt | Total | Private | Govt. | Total
July | 29375.96 | 1434.375 | 30810.335 | 29946.41 | 861.37 | 30807.78 | 101.9419 | 60.0519 | 99.9917
August | 29560.67 | 1437.145 | 30997.815 | 30658.16 | 1330.4 | 31988.56 | 103.7127 | 92.5724 | 103.1962
September | 29585.686 | 1749.046 | 31334.732 | 31463.2 | 1629.3 | 33092.5 | 106.346 | 93.1536 | 105.6096
October | 24705.302 | 1763.336 | 26468.638 | 26680.7076 | 1615.2838 | 28295.9914 | 107.9959 | 91.6039 | 106.9038
November | 17511.7 | 1116.945 | 18628.645 | 20157.575 | 1178.5107 | 21336.0856 | 115.1092 | 105.512 | 114.5337
December | 13064.74 | 945.86 | 14010.6 | 15466.77 | 1020.98 | 16487.75 | 118.3856 | 107.942 | 117.6805
January | 13479.986 | 1300.657 | 14780.643 | 13974.1376 | 1159.605 | 15133.7426 | 103.6658 | 89.1553 | 102.3889
February | 13286.844 | 1350.295 | 14637.139 | 13421.34 | 1155.702 | 14577.042 | 101.0122 | 85.5889 | 99.5894
March | 14776.1224 | 1149.1985 | 15925.3209 | 14441.683 | 938.754 | 15380.437 | 97.7366 | 81.6877 | 96.5785
April | 18776.214 | 1265.805 | 20042.019 | 18359.65 | 995.95 | 19355.6 | 97.7814 | 78.6812 | 96.5751
May | 24289.98 | 1202.285 | 25492.265 | 23718.65 | 1343.21 | 25061.86 | 97.6479 | 111.7214 | 98.3116
June | 27747.134 | 1700.745 | 29447.879 | 28650.02 | 2236.75 | 30886.77 | 103.254 | 131.5159 | 104.8862
Total | 256160.3384 | 16415.6925 | 272576.0309 | 266938.3031 | 15465.8155 | 282404.1187 | 104.2075 | 94.2136 | 103.6056
F.Y. 2019-20
Rs. in Million
Month | BILLING |  |  | COLLECTION |  |  | %AGE COLLECTION
| Private | Govt | Total | Private | Govt | Total | Private | Govt. | Total
July | 22852.805 | 1250.952 | 24103.757 | 22743.206 | 835.772 | 23578.978 | 99.5204 | 66.8109 | 97.8228
August | 27330.96 | 1563.02 | 28893.98 | 26261.51 | 1734.57 | 27996.08 | 96.087 | 110.9755 | 96.8924
September | 27009.516 | 1693.211 | 28702.727 | 27002.6249 | 1536.1933 | 28538.8182 | 99.9745 | 90.7266 | 99.4289
October | 24430.93 | 1852.686 | 26283.616 | 24449.0807 | 1778.6092 | 26227.6899 | 100.0743 | 96.0017 | 99.7872
November | 18829.388 | 1189.968 | 20019.356 | 18747.947 | 1352.6644 | 20100.6113 | 99.5675 | 113.6723 | 100.4059
December | 15336.53 | 1019.51 | 16356.04 | 15829.5 | 978.71 | 16808.21 | 103.2144 | 95.9981 | 102.7645
January | 14118.16 | 1351.421 | 15469.581 | 14495.168 | 1149.7572 | 15644.9252 | 102.6704 | 85.0776 | 101.1335
February | 12303.165 | 1395.274 | 13698.439 | 12439.4274 | 1234.9397 | 13674.3671 | 101.1075 | 88.5088 | 99.8243
March | 9940.559 | 934.358 | 10874.917 | 9025.5952 | 586.039 | 9611.6342 | 90.7957 | 62.721 | 88.3835
April | 12821.66 | 869.13 | 13690.79 | 6191.2085 | 609.5873 | 6800.7958 | 48.2871 | 70.1376 | 49.6742
May | 18348.274 | 1163.559 | 19511.833 | 11963.1565 | 745.0763 | 12708.2328 | 65.2004 | 64.0343 | 65.1309
June | 20696.672 | 1108.231 | 21804.903 | 21790.13 | 2059.94 | 23850.07 | 105.2833 | 185.8764 | 109.3794
Total | 224018.619 | 15391.32 | 239409.939 | 210938.5541 | 14601.8584 | 225540.4125 | 94.1612 | 94.8707 | 94.2068

## T&D
TRANSMISSION & DISTRIBUTION (T&D) LINE LOSSES (MONTH WISE)
FOR THE YEAR 2020-2021
M E P C O | [6 empty] | Mil. KWH
Month | 2020-2021 |  |  |  | 2019-2020 |  |  |  | INC/ DEC | Target (BOD)
| UNITS RECVD | UNITS BILLED | UNITS LOST | %AGE LOSS | UNITS RECVD | UNITS BILLED | UNITS LOST | %AGE LOSS
July | 2483.1463 | 1978.4481 | 504.6982 | 20.3249 | 2465.3529 | 1952.2521 | 513.1009 | 20.8125 | -0.48752 | 20.1594
August | 2642.4588 | 2127.8305 | 514.6283 | 19.4754 | 2481.7738 | 1996.8127 | 484.9611 | 19.5409 | -0.065552 | 18.9277
Prog: | 5125.6051 | 4106.2786 | 1019.3265 | 19.8869 | 4947.1268 | 3949.0647 | 998.062 | 20.1746 | -0.28763 | 19.5415
September | 2181.693 | 1926.0829 | 255.6101 | 11.7161 | 2358.6902 | 2065.8027 | 292.8875 | 12.4174 | -0.70124 | 12.0277
Prog: | 7307.2981 | 6032.3615 | 1274.9366 | 17.4474 | 7305.8169 | 6014.8674 | 1290.9495 | 17.6702 | -0.22272 | 17.1157
October | 1599.0076 | 1438.4089 | 160.5987 | 10.0436 | 1429.9188 | 1274.9989 | 154.9199 | 10.8342 | -0.79053 | 10.4942
Prog: | 8906.3056 | 7470.7703 | 1435.5353 | 16.1182 | 8735.7357 | 7289.8663 | 1445.8694 | 16.5512 | -0.43301 | 16.0318
November | 1003.1782 | 979.3289 | 23.8493 | 2.3774 | 1009.7783 | 982.7027 | 27.0756 | 2.6813 | -0.30397 | 2.5972
Prog: | 9909.4838 | 8450.0992 | 1459.3846 | 14.7272 | 9745.514 | 8272.569 | 1472.945 | 15.1141 | -0.38693 | 14.6398
December | 972.0761 | 866.596 | 105.4801 | 10.851 | 944.458 | 825.2731 | 119.1849 | 12.6194 | -1.7684 | 12.2234
Prog: | 10881.56 | 9316.6953 | 1564.8647 | 14.3809 | 10689.972 | 9097.8421 | 1592.1299 | 14.8937 | -0.51279 | 14.4263
January | 1031.0493 | 976.546 | 54.5033 | 5.2862 | 920.3432 | 877.6161 | 42.7271 | 4.6425 | 0.64368 | 4.4968
Prog: | 11912.6093 | 10293.2412 | 1619.368 | 13.5937 | 11610.3152 | 9975.4582 | 1634.857 | 14.0811 | -0.48734 | 13.6392
February | 1025.7411 | 979.519 | 46.2221 | 4.5062 | 928.4567 | 897.9945 | 30.4623 | 3.281 | 1.2253 | 3.178
Prog: | 12938.3503 | 11272.7602 | 1665.5902 | 12.8733 | 12538.7719 | 10873.4526 | 1665.3193 | 13.2814 | -0.40808 | 12.8646
March | 1409.7112 | 1147.9767 | 261.7344 | 18.5665 | 893.9309 | 730.1411 | 163.7897 | 18.3224 | 0.24411 | 17.7475
Prog: | 14348.0615 | 12420.7369 | 1927.3246 | 13.4326 | 13432.7028 | 11603.5937 | 1829.109 | 13.6168 | -0.18419 | 13.1896
April | 1730.0659 | 1471.245 | 258.8209 | 14.9602 | 1473.5478 | 1253.7988 | 219.749 | 14.9129 | 0.047255 | 14.445
Prog: | 16078.1275 | 13891.9819 | 2186.1455 | 13.597 | 14906.2506 | 12857.3926 | 2048.8581 | 13.745 | -0.14794 | 13.3137
May | 2232.3306 | 1768.8154 | 463.5153 | 20.7637 | 2128.6447 | 1687.6414 | 441.0033 | 20.7176 | 0.046175 | 20.0675
Prog: | 18310.4581 | 15660.7973 | 2649.6608 | 14.4708 | 17034.8953 | 14545.0339 | 2489.8614 | 14.6162 | -0.14549 | 14.1576
June | 2221.7514 | 1805.2933 | 416.4582 | 18.7446 | 2289.784 | 1836.9148 | 452.8693 | 19.7778 | -1.0332 | 19.1572
Prog: | 20532.2095 | 17466.0906 | 3066.1189 | 14.9332 | 19324.6793 | 16381.9487 | 2942.7306 | 15.2278 | -0.29462 | 14.75